Hong Kong Institute of Vocational Education

HD of Automotive Engineering
Visit Report 1
Name: Cheung Chi Wai 

Class: 91305/3 (7)

Venue: LPG vehicles workshop, HK IVE LWL, Kowloon tong   

Objective: Statement of legal requirement for LPG vehicles and stat the component of LWL LPG vehicles workshop.

Legal Requirement of LPG vehicles workshop:

General

1.1 This section sets out the gas safety requirements for LPG vehicle workshops and precautions

for any work on LPG fuelled vehicles carried out in the workshops.

1.2 Only LPG vehicle workshops that have been approved by the Gas Authority shall carry out

maintenance and repair work on the fuel system of an LPG vehicle.

1.3 Construction and use approval of an LPG vehicle workshop shall be obtained from the Gas

Authority before its construction and use.

2 Location

2.1 An LPG vehicle workshop shall be readily accessible in a well-ventilated area at ground level,

and never in cellars or in basements. A workshop located on upper floors may be considered

under special circumstances with a well-ventilated access road.

2.2 An LPG vehicle workshop should not be located in the same building as residential

accommodation.

2.3 Drains or unventilated pits shall be avoided in the workshop floor area or in the immediate

vicinity of the workshop. Where a gully or drain is unavoidable, the opening shall either be

securely covered or the drain suitably sealed.

2.4 The perimeter of the repair bay shall be marked conspicuously on the ground. It shall extend

500mm beyond the sides and fenders of the largest vehicle intended to be serviced.

2.5 Warning signs showing “LPG Vehicle Workshop / 石油氣車維修工埸” and “No Smoking /

不准吸煙” shall be prominently displayed at the workshop area.

3 Ventilation

General

3.1 The design of an LPG vehicle workshop shall be such that the occurrence of a build-up of an

LPG/air mixture above the lower flammable limit is minimized by provision of adequate

ventilation.

3.2 Wherever possible, adequate natural ventilation should be provided, but where adequate natural

ventilation is unattainable, mechanical ventilation shall be provided as an alternative.

3.3 An LPG vehicle workshop shall be ventilated utilizing air inlets and outlets arranged to provide

air movement across the floor as uniformly as practicable.

3.4 Ventilation apertures and/or ducts shall be positioned in such a way so as to prevent

accumulation of LPG.

Natural Ventilation

3.5 Apertures for natural ventilation shall be situated in external walls of an LPG vehicle workshop

such that:-

(i) the bottoms of low level ventilation apertures are not more that 150 mm above the floor;

(ii) the tops of high level ventilation apertures are not more than 500 mm below the ceiling;

(iii) the effective low level ventilation area is within 500 mm from the floor; and

(iv) the effective high level ventilation area is within 1000 mm from the ceiling.

3.6 Ventilation apertures shall be provided with a total effective area of at least 0.03 m2 per square

metre of floor area at low level and 0.015 m2 per m2 of floor area at high level.

3.7 Ventilation apertures shall be at least 1 m from openings into other buildings or any fixed

source of ignition.

Mechanical Ventilation

3.8 A minimum ventilation capacity of 500 litre/s per vehicle shall be provided for mechanical

ventilation systems in the workshop area.

3.9 The airflow velocity within any exhaust duct of the ventilation system shall not be less than 5

m/s.

3.10 The inlet apertures of the ventilation duct system shall be located at not more than 150 mm

above the floor level.

3.11 The outlet of the ventilation system shall discharge at least 1.5 m away from any opening into

the workshop, adjacent buildings, or any fixed source of ignition.

3.12 A clearance of 150 mm shall be maintained around the air intakes of the ventilation system to

prevent blockage of the inlet openings.

3.13 All electrical apparatus for a mechanical ventilation system shall be of flameproof type and be

suitable for use in one 1 hazardous areas in compliance with BS 5345 or equivalent.

3.14 An audio and visual alarm system indicating failure of the mechanical ventilation system such

as interruption of electrical supply, failure of extraction fan, etc. shall be provided for the

system. Emergency procedures in response to the alarm shall be prominently displayed in the

workshop area.

3.15 The ventilation system shall be started before the work commences and be kept operating

whilst the work is in progress.

4 Gas Detection System

4.1 Gas detectors shall be calibrated for detection of LPG and be located at not more than 150 mm

above the floor level around the workshop.

4.2 A gas detection system shall provide an audible and visual alarm, if there is a flammable gas

mixture above 20% of the lower flammable limit.

4.3 The detection system shall be capable of activating the mechanical ventilation system if the

system is not switched on.

5 Fire Protection

5.1 At least 2 fire extinguishers of dry powder type shall be provided at the workshop.

5.2 Other fire services requirements shall be adhered to as may be stipulated by the Director of Fire

Services.

6 Safety Precautions

6.1 Inside the workshop, unless a vehicle has been tested and a leak-free condition has been

verified:-

(i) the space in the vicinity of 3m from the perimeter of the vehicle to a height of 1m above

the highest point of the LPG fuel system should be classified as Zone 1;

(ii) ignition sources shall be kept out of the hazardous zone; and

(iii) the gas outlet valve of the LPG cylinder shall be closed at all times, except when

checking or testing is being carried out which requires the gas.

6.2 Heating, welding, or flame cutting shall not be carried out within 1m of the LPG cylinder.

6.3 All electrical installations or appliances for use in Zone 1 area shall be of flameproof type in

compliance with BS 5345 or equivalent.

6.4 No smoking is allowed in the workshop area.

6.5 Portable combustible gas detectors shall be kept readily available for gas leak detection.

7 Personnel

7.1 Only competent persons who have successfully completed the training course offered by the

Vocational Training Council and enlisted by the Gas Authority shall carry out work on the LPG

fuel system of a vehicle.

8 General Service Workshop

8.1 Workshops which may require to do work on the vehicle (e.g. brake repair) but not on the LPG

fuel system up to the outlet of the regulator should not be required to have a competent person.

8.2 The workshop shall equip a gas detector with alarm setting at 20% of the lower flammable

limit.
Special components of LWL LPG vehicles workshop:

There have a LPG indicator to test the LPG amount in air, if there are too much LPG in air ,alarm will be buzzed.

A direct link to police ,fire station and hospital. Rescue can be known without ringing 999.   
