# The flow of fluids in pipes

The head lost due to friction may best be determined by the use of the Darcy equation.

The pressure loss per unit length of pipe is given by

∆P = Pressure Loss (N/m2)

ρ = Density of water (kg/m3)

# Pipe fittings

The pressure loss in the local resistances is generally expressed in terms of fractions of the velocity pressure

where k is a velocity pressure factor for the local item concerned as determined by experiment.

Consider the straight pipe having a length “L” from “1” to “2” and containing a valve then if ∆P/l = pressure loss per unit length of straight pipe, then

# Pump head calculation

PUMP HEAD = STATIC HEAD + PIPE FRICTION + INDEX PRESSURE

- Check the flow rate

COP gives 900 l/min. or 15 l/s

Pressure at outlet 4 to 7 bar

- Pipe size

CIBSE Guide C4 – Table C4.21 Flow of water at 10oc galvanised pipes

100 diameter G.I. pipe

Flow rate(M): 15.7 l/s

Pressure loss (∆Pl): 400 Pa/m3

Velocity(v): 1.9 m/s

- Assume:	15no. Elbow

3 no. Gate valve

1 no. Check valve

|  |  |  | K |  | EL ( l e ) |  | (m) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (A) | 15 | x | 0.3 | x | 4.5 | = | 20.25 |
| (B) | 3 | x | 0.1 | x | 4.5 | = | 1.35 |
| (C) | 1 | x | (0.08x100) | x | 4.5 | = | 36 |
|  |  |  |  |  |  |  | 57.6 (say 58) |

- Measured pipe length = 60 + 30 = 90m

- Total effective pipe length = pipe length + fitting equivalent pipe length

90 + 58 = 148 (effective pipe length)

∆P of pipe = 400 Pa/m

- Pump head = Static Head + Total effective pipe length + Index pressure

Pump head = 60 + 6 + 40 = 106m

- Specify pump duty as 15.0 l/s against 106m (head)

N.B. quick selection method

(60 + 30) x 1.5 to 1.75 = 135 to 157m or 146 average

# Transfer pump design & calculation

- Transfer pump flow rate

The 30m3 supply water tank for F.H./H.R. is to be filled within 6 hours (based on good practice an accepted by F.S.D.)

- Pump riser pipe size

Flow rate: 1.67 l/s

Pipe size: 50mm diameter G.I. pipe

Velocity: 2m/s or (below 1.5m/s)

Pressure loss per unit length: 200-600 Pa/m

- Pipe friction calculation

| No. | Description of fitting | K | EL | m |
| --- | --- | --- | --- | --- |
| 10 | Elbow | 0.5 | 1.7 | 8.5 |
| 3 | Gate valve | 0.3 | 1.7 | 1.53 |
| 2 | Check valve | 0.08 x 50 | 1.7 | 13.6 |
|  |  |  |  | 23.63 (say 24) |

- Assume: 	Static Head 60m

Pipe length 60 + 30 = 90 m

- Total effective pipe length = pipe length + fitting equivalent pipe length

90 + 24 = 114

∆P = 222.5 Pa/m

- Pump head = Static Head + Total effective pipe length + Index pressure

Pump head = 60 + 3 + 0 = 63m

- Specify pump duty as 1.67 l/s against 63m (head)

# Transfer tank size

  - Pump flow rate: 1.67l/s

  - 5 – 20 minutes

Result: Tank volume = 20 min. x 60 s/min. x 1.67 l/s = 2004 litres

# Inflow rate for transfer tank