PROPOSED A & A WORKS AT xxxxxxxxxxxxxxxxxxxxxxx

F.S. NOTE

### NOTES FOR AUTOMATIC SPRINKLER SYSTEM

- AUTOMATIC SPRINKLER SYSTEM SHALL BE RETAINED IN ACCORDANCE WITH THE RULES FOR THE AUTOMATIC SPRINKLER INSTALLATIONS AND TO THE H.K.F.S.D.’s REQUIREMENTS.

- UPON ACTUATION OF AUTOMATIC SPRINKLER SYSTEM, THE EXISTING SPRINKLER PUMPS SHALL BE OPERATED IMMEDIATELY.

- THE DRAIN PIPE OF SPRINKLER ALARM VALVE, DRAIN VALVE AND TEST VALVE SHALL BE DISCHARGED TO A CONSPICUOUS POSITION WITH NO POSSIBILITY OF BEING SUBMERGED.

- ONCE THE EXISTING DUTY PUMP OR THE STANDBY PUMP HAS STARTED, IT CAN ONLY BE STOPPED MANUALLY.

### NOTES FOR FIRE HYDRANT AND HOSE REEL SYSTEM

- HOSE REEL SYSTEM SHALL BE RETAINED IN ACCORDANCE WITH THE CODE OF PRACTICE FOR MINIMUM FIRE SERVICE INSTALLATIONS AND EQUIPMENT OF THE HONG KONG FIRE SERVICES DEPARTMENT (H.K.F.S.D.).

- THE FIRE HYDRANT AND HOSE REEL SYSTEM SHALL BE PROVIDED BY CONNECTING FROM THE EXISTING FH/HR WATER TANK AND FIXED FIRE PUMPS.

- EVERY PART OF THE RENOVATED AREA SHALL BE REACHED BY A LENGTH OF NOT MORE THAN 30 METRES OF HOSE REEL TUBING.

- FOR ANY TWO HYDRANT OUTLETS WITH A FLOW OF 450 L/MIN OF EACH OUTLET, THE MINIMUM RUNNING PRESSURE SHALL BE OF 350kPa, THE OUTLET PRESSURE OF EACH FIRE HYDRANT SHALL NOT EXCEED 850kPa. PARITY VALVE/RATIO TYPE PRESSURE REDUCING VALVE SHALL BE PROVIDED TO MAINTAIN A PRESSURE OF 850kPa MAXIMUM TO 350kPa MINIMUM RUNNING PRESSURE RANGE AT ANY ONE HYDRANT.

- UPON ACTUATION OF ANY HOSE REEL SET, AUDIBLE AND VISUAL ALARM SIGNALS SHALL BE REGISTERED ON AFA CONTROL PANEL, THE ALARM BELL SHALL BE SOUND AND THE EXISTING FIXED FIRE PUMPS SHALL BE OPERATED IMMEDIATELY.

### NOTES FOR AUTOMATIC AND MANUAL FIRE ALARM SYSTEM

- AUTOMATIC DETECTION SYSTEM SHALL BE RETAINED IN ACCORDANCE WITH THE F.O.C. RULES FOR AUTOMATIC FIRE ALARM INSTALLATIONS FOR THE PROTECTION OF PROPERTY AND TO THE H.K.F.S.D.’s REQUIREMENTS.

- NEW AUTOMATIC AND MANUAL FIRE ALARM (AFA) CONTROL PANEL FOR THE RENOVATED AREAS SHALL BE PROVIDED AT THE EXISTING F.S. CONTROL ROOM. ALL FIRE SIGNALS FROM THE NEW AUTOMATIC AND MANUAL FIRE ALARM CONTROL PANEL SHALL BE FULLY REPEATED TO THE NEW REPEATED PANEL PROVIDED AT THE BASEMENT LEVEL 1 MANAGEMENT OFFICE.

- THE NEW AFA CONTROL PANEL SHALL BE CONNECTED TO THE FIRE SERVICES COMMUNICATION CENTRE BY A DIRECT TELEPHONE LINK.

- ALL NEW AFA CONTROL PANEL AND SMOKE / HEAT DETECTORS SHALL BE COMPATIBLE WITH THE EXISTING SYSTEM.

- AN AUTOMATIC FIRE DETECTION AND ALARM SYSTEM SHALL BE PROVIDED TO GROUND FLOOR MECHANICAL AND ELECTRICAL ROOMS, AND THE THREE BASEMENT FLOORS, BUT EXCLDING THE MECHANICAL & ELECTRICAL RISER DUCTS.

- VISUAL FIRE ALARM SYSTEM WILL BE PROVIDED TO THE ARCADES AND TOILETS FOR PUBLIC USE ONLY IN ACCORDANCE WITH “DESIGN MANUAL BARRIER FREE ACCESS 1997” AND H.K.F.S.D. CIRCULAR LETTER NO. 4/2001.

### NOTES FOR SMOKE EXTRACTION SYSTEM

- NEW DYNAMIC SMOKE EXTRACTION SYSTEM SHALL BE INSTALLED IN ACCORDANCE WITH THE CODES OF PRACTICE FOR MINIMUM FIRE SERVICE INSTALLATIONS AND EQUIPMENT AND INSPECTION, TESTING AND MAINTENANCE OF INSTALLATIONS AND EQUPMENT. JUNE 1998.

### NOTES FOR STAIRCASE PRESSURIZATION SYSTEM

- NEW STAIRCASE PRESSURIZATION SYSTEM SHALL BE INSTALLED IN ACCORDANCE WITH THE CODES OF PRACTICE FOR MINIMUM FIRE SERVICE INSTALLATIONS AND EQUIPMENT AND INSPECTION, TESTING AND MAINTENANCE OF INSTALLATIONS AND EQUPMENT. JUNE 1998.

### NOTES FOR EMERGENCY GENERATOR

- EMERGENCY POWER SUPPLY SHALL BE PROVIDED BY CONNECTING FROM THE EXISTING EMERGENCY GENERATOR TO PROVIDE SUFFICIENT ELECTRICAL CAPACITY FOR THE EMERGENCY LIGHTINGS, EXIT SIGNS, DYNAMIC SMOKE EXTRACTION SYSTEM, STAIRCASE PRESSURIZATION SYSTEM AND FIRE SERVICES INSTALLATION, IN THE EVENT OF MAIN POWER FAILURE.

### NOTES FOR EMERGENCY LIGHTINGS

- EMERGENCY LIGHTINGS SHALL BE PROVIDED THROUGHOUT THE RENOVATED AREA AND ALL EXIT ROUTES LEADING TO OPEN AREA. EMERGENCY LIGHTINGS SHALL BE CONNECTED TO THE EMERGENCY POWER SUPPLY SYSTEM.

### NOTES FOR EXIT SIGNS

- SUFFICIENT EXIT SIGNS SHALL BE PROVIDED AS PER DRAWINGS SO THAT ALL EXIT ROUTES WITHIN THE RENOVATED AREA ARE CLEARLY INDICATED.

### NOTES FOR PORTABLE FIRE EXTINGUISHERS

- PROPER SIZE AND TYPE OF PORTABLE HAND OPERATED FIRE EXTINGUISHERS OF NON-HALON BASED TYPE APPROVED BY H.K.F.S.D. SHALL BE PROVIDED AT POSITIONS AS INDICATED ON PLANS, AND SHALL BE IN ACCORDANCE WITH H.K.F.S.D. REQUIREMENTS.

### NOTES FOR VENTILATION AND AIR-CONDITIONING CONTROL (VAC) SYSTEM

- WHEN A VENTILATION/AIR-CONDITIONING CONTROL SYSTEM TO THE RENOVATED AREA IS PROVIDED, IT SHALL STOP THE MECHANICALLY INDUCED AIR MOVEMENT WITHIN A DESIGNATED FIRE COMPARTMENT IN ACCORDANCE WITH THE H.K.F.S.D. REQUIREMENTS.

### NOTES FOR OTHER REQUIREMENTS ON MECHANICAL AND ELECTRICAL INSTALLATIONS

- ALL ELECTRICAL CIRCUITS SHALL BE PROTECTED BY MINIATURE CIRCUIT BREAKERS.

- ALL LININGS FOR ACOUSTIC AND THERMAL INSULATION PURPOSES IN DUCTING AND CONCEALED LOCATIONS SHALL BE OF CLASS 1 OR 2 RATE OF SURFACE SPREAD OF FLAME AS PER BRITISH STANDARD 476 PART 7 1971 (REVISED 1987) OR ITS INTERNATIONAL EQUIVALENT, OR BE BROUGHT UP TO THAT STANDARD BY USE OF AN APPROVED FIRE RETARDANT PRODUCT.

- ALL LINING FOR ACOUSTIC, THERMAL INSULATION AND DECORATIVE PURPOSES WITHIN PROTECTED MENAS OF ESCAPE SHALL BE OF CLASS 1 OR 2 RATE OF SURFACE SPREAD OF FLAME AS PER BRITISH STANDARD 476 PART 7 1971 (REVISED 1987) OR ITS INTERNATIONAL EQUIVALENT, OR BE BROUGHT UP TO THAT STANDARD BY USE OF AN APPROVED FIRE RETARDANT PRODUCT.