| Location | Noise rating NR | Pipe material |
| --- | --- | --- |
|  |  | Metal: copper, stainless, steel, galvanised (m/s) | Plastic: UPVC, ABS, CPV, Pd (m/s) |
| Service duct, riser, shaft, plant room | 50 | 2.0 | 2.5 |
| Service enclosure, ceiling void | 40 | 1.5 | 1.5 |
| Circulation area, entrance corridor | 35 | 1.5 | 1.5 |
| Seating area, lecture/meeting room | 30 | 1.25 | 1.25 |
| Bedroom | 25 | 1.0 | 1.0 |
| Theatre, cinema | 20 | 0.75 | 0.75 |
| Recording studio | <20 | 0.5 | 0.5 |