UNLESS OTHERWISE STATED, BRANCH PIPE SIZE SHALL BE AS FOLLOW:

WASTE BRANCH FOR BASIN

1 no.   	32 mm

2-3 no.	40 mm

4-5 no.	50 mm

5 or more	65 mm

WASTE BRANCH FOR EACH KITCHEN SINK		40 mm

WASTE BRANCH FOR EACH FLOOR DRAIN IN TOILET	50 mm / 40 mm

VENT BRANCH FOR EACH WATER CLOSET		50 mm

VENT BRANCH FOR EACH URINAL			40 mm

SOIL BRANCH FOR EACH WATER CLOSET		100 mm

SOIL BRANCH FOR URINAL

1 no.	40 mm

2-3 no.	50 mm

4-6 no.	65 mm

7 or more	80 mm

The hot water taps shall be fixed at a distance from a hot water apparatus or from a flow and return system not greater than 12m for pipes up to and including 20mm diameter, 8m for pipes up to 25mm diameter, and 3m for pipes above 25mm diameter.

| Flushing Water Point | Pipe Size |
| --- | --- |
| 1-3 | 20 |
| 4-7 | 25 |
| 8-11 | 32 |
| 12-23 | 40 |

| Cold Water Point | Pipe Size |
| --- | --- |
| 1-3 | 22 |
| 4-6 | 28 |
| 7-10 | 35 |
| 11-16 | 42 |

Assumption (From WSD)

CW – Based on 135 l per flat for 1st floor to 10th floor and 90 l per flat for additional flat.

FW – Based on 45 l per water point.

| Size of branch discharge pipe or discharge stack D | Size of branch ventilation pipe or stack |
| --- | --- |
| Smaller than 75mm | 2/3 D (25mm min.) |
| 75mm and above | ½ D |

An overflow or warning pipe shall be provided and this pipe shall at last be one commercial pipe size larger than the inlet pipe.

For Example:

| Dia. 80 “inlet pipe | Dia. 100 overflow pipe |
| --- | --- |