PRASAR BHARATI

BROADCASTING CORPORATION OF INDIA

O/O CHIEF ENGINEER (SZ) AIR & TV

CHENNAI

CESZ/SMT/GD/2007                                                                               07-08-2007

CIRCULAR

Sub: Earthing arrangement for FM Towers where

AIR FM Transmitter and  LPT TV centre are cocited.

                            It has been noticed that where AIR FM Transmitter and LPT TV centres are co cited the LPT antenna is installed at the top of the FM Tower, but Lightning arrestor probe from the top of the TV antenna is connected just over the top platform with nut and bolt.  For effectively discharging the Lightning to earth without affecting FM /LPT equipment it is suggested to run exclusive Copper strip/copper cable and connect to the earth grid at the bottom of the tower. The earth grid may be formed by interconnecting all the 4 tower leg earths through copper strip and brazing. The copper cable may be connected to earth grid by brazing in addition to nut and bolt connection. 

                             TV project section has procured required copper cable and despatched to such LPT centres. 135 Mt length of 50 sq mm multi-strand copper cable has been sent each to LPT centres viz  Chitradurga, Devikulam, Kannur, Karaikal, Karwar, Madikere, Markapur and Nagercoil. 100Mt length of 50sq mm multi-stranded copper cable has been sent each to LPT Tirupathy and LPT Manjeri.

                              The concerned FM stations are requested to coordinate with LPT TV centre and arrange to provide the earthing arrangement of Lightning arrestor as suggested above and send compliance.

                                                                                     ( R.Jeyakumar)

                                                                               Deputy Director (Engg)

To                                                                           For Chief Engineer (SZ)

Station Engineer/Assistant Station Engineer/Assistant Engineer

AIR,  Chitradurga, Devikulam, Kannur, Karaikal, Karwar, Madikere, Markapur, Nagercoil, Tirupathy, Manjeri, 

Copy to 

1. TV Project Section,

    ( By Name : Sh. S. Natarajan, DDE ) CESZ AIR & TV Chennai—

           With reference to note dated 11-07-2007 from TV project wing.

2. TV maintenance Section,

   ( By name: Sh. T.S. Thiagarajan, DDE) CESZ AIR & TV Chennai---

With a request to advise the concerned LPT TV centres accordingly.

                                                                            For Chief Engineer (SZ)

