PRASAR BHARATI

(Broadcasting Corporation of India)

OFFICE OF THE CHIEF ENGINEER (SOUTH ZONE)

ALL INDIA RADIO & TELEVISION

Swami Sivananda Salai, Chennai - 600 005.

CESZ/SMT/GD/2007                                                            14-12-2007  

                                                  CIRCULAR  

Sub: Common Technical inspection points


During technical inspection of the stations, it has been observed that the following points need prompt attention by most of the stations.

1. The C-band dish lightening arrestor is to be modified with lightening arrestor of suitable length so that the lighting arrester will be at a higher level than the LNBC and is to be earthed firmly using 25sqmm multi strand insulated copper cable. The earthing cable is to be suitably routed in such a way that it should not obstruct the tuning of the dish in any way.

2. The complete terrace of the studios, office block and ancillary structure are to be cleared of dry leaves and wild growth immediately to prevent damage to the waterproof treatment and seepage of water into the building.   At regular intervals, it is to be ensured that all the wild growth are removed and water drainpipes are cleared off from accumulation of dry leaves preventing free flow of rainwater
3. Plan showing the location of earth pits for the complete complex is to be prepared, laminated and displayed in the LT room & control room/transmitter hall at studios and transmitter. All the earth pits are to be designated and watering to be done regularly.

4. Plan showing the location of fire fighting equipments including fire buckets and fire hydrants is to be prepared, laminated and displayed at the entrance of the studios and transmitter for easy identification during emergency. All the fire fighting equipments, fire buckets and fire hydrants including hosepipe are to be maintained in good condition at all time. Testing and maintenance of fire fighting equipments are to be entered in the fire fighting equipments register.

5. We have come across several points, which are routine in nature and are not attended to by stations in spite of having been pointed out for suitable action in the previous technical inspection reports. As stations are aware a blank proforma for our technical inspection is already available in geocities and stations should take this as a reference, guidance and direction to run the station and maintain equipments and registers on daily basis. But unfortunately, we find that new registers are being opened only a few days in advance to our inspection.

6. All stations are therefore requested to ever remain complied with these points, as our recommendation for best Maintained Stations Award is based on this aspect also.

7. Engineering heads are requested to keep a power point presentation of the history and development of the station to it present status with neat sketches and photos, of lands and buildings, lay out of studios and equipment, as very often it is seen that only very limited staff are aware. This will ensure that all the key engineering officers in the station who are new will get quick information in one place and will get benefited by it.  The presentation may be prepared before 31.03.08 and a copy sent to zonal office.

 R. Periaswamy

Assistant Director (AVM)

For Chief Engineer (SZ)             

To

Engineering Heads of all stations in South Zone                                                                                                  

