NFS-320

CONVERTIFIRE

converts legacy databases to ONYX databases.

Identifies issues

Converts AFP-300/400 to NFS2-640

Converts AFP-300 to NFS-320

Converts AFP-200 to NFS2-640/320

NFS-320/NFS2-640

2007

Small applications

Integrated power supply, keypad/display, 1 loop, 318 points, 4 NACS

Includes everything but batteries

320 CPU same as CPU2-640 except:

320 only 1 loop

Keypad in different location than 640, cannot mount in CAB-4 box

FIREVOICE 25/50

320 can interface to NFV-25/50Z5 voice evac system to control messages & speakers

Done thru software zone programming

EIA-485 connection

Single channel voice evac systems

ACS programming consists of making address 01 as GROUP M

For more than 8 speaker circuits, it can be expanded with NFV-25/50Z5, distributed audio panels

Provides 24 speaker circuits controlled by serial link

SINGLE CHANNEL

Sends only one message at any one time, multiple messages sent one at a time.

EVAC message sent to threat zone, then alert sent to outside zones

Multiple channel send out multiple messages to multiple speakers/circuits at same time

IPDACT-2 & IPDACT-2UD

October 14/2009 received UL with 320

NFS-320SYS

January 1/2010

Installed in CAB-4 cabinet

Allows retrofit of legacy panels B,C, or D size cabinets

Technical bulletins

TB10-03-01	NFS2-640 Firmware v.12.003.001 March 1/2012

Could affect NFS2-640 using v.12.000.004 thru 12.001.005

Activation of FCM-REL on one SLC loop may interrupt regular SLC communication on the other loop, provided there are NO MODULES on the 2nd loop.

If FCM-1-REL on loop 1 is activated, polling will be inhibited on loop 2 and NO trouble indicated, although a NO DEVICES INSTALLED trouble will come in.

OCCURS WHEN:

2-640 is 2 loops

2-640 firmware V12.000.004 thru 12.001.005

2-640 operating in FLASHSCAN

FCM-1-REL installed on one loop and the other loop does not have any modules.

Usually discovered during VI

Affects Oct/2008 to Feb/2010 products

DOES NOT affect NFS-320 or NFS2-3030

RECOMMENDED UPGRADE to v12.003.001

If all 4 conditions exist, upgrade ASAP

TB-09-12-01	NFS2-640 & NFS-320 FIRMWARE UPGRADE

DECEMBER 7/2009

March 31/2009 – availability of v.12.1.5 to fix AC FAIL conditions on NFS2-640 and       NFS-320

REQUIRE upgrade of all NFS2-640 and NFS-320s to v.12.1.5

Failure to do so may result in reduced life expectancy of power supply

Ref. TB09-03-01

TB07-12-01	NFS-320 & NFS2-640 BATTERY TROUBLES

KAPS-24 v.1.0 power supply

Panels shipped before 11/30/07

May cause panel to enter false BATTERY TROUBLE or CHARGER FAULT even tho batteries are ok

Identified on label on U12EPROM

Marked as KAPSV1.00

Version 1.1 fixes issue

Anything after 12/03/07 is ok.

Check following PRIOR to upgrade:

Ensure batteries are 18AH to max 200Ah

Batteries less than 3 years old

If programmed by VERIFIRE TOOLS, make sure battery charger parameters are set

SOFTWARE USED TO RECONFIGURE LEGACY TO ONYX: SPECI-FIRE (??)

TB07-09-01 NFS2-640, NFS-320 RELEASING TYPE CODES W/VERIFIRE TOOLS 5.0

SEPTEMBER 17/2007

Affects modules with releasing type code labels using VFT 5.0

VFT 5.0 released 8/20/07

Affects SLC loop in either FLASHSCAN or CLIP mode

Will default Flashscan to NULL whe using point program serv menu

Affected modules will display as INVALID REPLY

When using Excel v5, will default to RELEASE, will display INVALID REPLY

Specific to nodules with releasing type code labels & programmed with v5.0

Also affects database upgrades w/v5.0 where modules have been edited or added.

Affects v5.0 from PC, laptop, NCS, or ONYXWORKS

Correct by manually programming valid flashscan type, either CONTROL or RELAY

NTSRUNTIMETPL.MDB

NFS2-3030

CONVERTIFIRE – converts 2020, AFP-1010 to NFS2-3030

AMPS-24/E

Primary power supply for 2-3030 (Sept/09)

Additional power available for main & auxillary outputs. Auxillary can be disabled.

Charges 7-200Ah batteries

Selectable charger current

5 point trouble reporting (added charger fault)

USB programmable

DOCUMENT 51907 for Install/Maint

Configured with PK-PPS sorftware

GAS DETECTION

NFS2-3030 interfaces to industry standard 4-20mA devices using FMM-4-20 module

FMM-4-20 connects to 2-3030 via SLC to collect, display, act on data received from gas or flame detectors, etc.

FMM-4-20

User programmed for up to 5 event thresholds, based on concentration level of gas being monitored

Executes appropriate pre-programmed response

Can be labelled as any:

Fire, security, non-fire trouble, pre-alarm, non-fire & critical process

NETWORK DISPLAY MODE

System Release 4 adds Network Display Mode

Allows 2-3030 to act as Network Annunciator for up to 4 DVC nodes and 1 other ONYX control panel

Eliminates expense of adding NCA2 to small networks

Mapping network node to 2-3030 on Network Mapping Menu will allow the 2-3030 to monitor & annunciate events for that node

Drill mapping for 2-3030 can only be changed thru VFT

In network mode, 2-3030 hasa ability to perform network ACK, RESET, SIG SIL, AUTO SILENCE and DRILL

Only on network nodes mapped to 2-3030 will be affected

Initiating AC, RESET, SIG SIL or DRILL on network node mapped to 2-3030 may affect nodes not participating in NETWORK DISPLAY MODE thru logic zone programming

Participating ONYX panel is mapped in the same manner as the NCA-2

3rd panel settings screen has been added to programming menu:

Network Display Mode: ON

Drill Mode: CUSTOM

TB10-07-02 FSB200/FSB-200S BEAM DETECTORS, USE OF ALARM VERIFICATION WITH BEAM DETECTORS AND NFS-3030/NFS2-3030 LCM FIRMWARE UPGRADE NOTICE

JULY 12/2010

FSB-200/200S

20 second alarm verification timer to help with false alarms

ISSUE: detectors programmed for alarm verification in 3030 & 2-3030 operating LCM firmware v.2.8.14 thru 3.3.2 WILL NOT initiate alarms

Detectors NOT programmed for alarm verification are NOT affected & will work.

DEFAULT is NO Alarm Verification

NFS2-640 & NFS-320 are NOT AFFECTED

Issue would be found during VI

Affected LCM-320 loop cards were manufactured May/05 to June/10

LCM firmware v.4.1.3 fixes issue

LCM-320 after 8/1/10 are ok

If more than 20 seconds required, LCM-320 needs upgrade to v.4.1.3

If 20 seconds not needed, DO NOT program it

TB09-09-01 LCM FIRMWARE V.3.2.4 RELEASED ADDRESSES OPEN CIRCUIT CONDITIONS ON XP10-M & FMM-1 MODULES

SEPTEMBER 28/09

XP10-M operating in flashscan or CLIP

If wired Class A, open circuit on initiating device ckt will initially cause open circuit trouble but will change to INVALID REPLY

Once in INVALID REPLY , module will continue to process active events on feed side of the circuit.

Active events on the return side will not be detected.

Specific  to Class A with open .

Other Class A circuits on the same card are not affected.

Class B NOT affected.

FMM-1A in Class A or Class B on heavily loaded SLC loops operate in CLIP mode

Event activations from CLIP mode, FMM-1A with open circuit trouble may be delayed to reporting to panel. Delayed reporting depends on total # of detectors on loop.

80+ detectors will affect FMM-1 reporting times

v.3.2.4 corrects issue

NFS2-3030 requires upgrade of LCM and 2-3030 firmware

3030 requires just upgrade of LCM as 3030 firmware has not changed

LCM-320s shipped after 9/28/09 are v.3.2.4

TB-07-08-01 ACCLIMATE DETECTORS

AUGUST 20/07

Acclimate smokes (FAPT751/851) connected to 3030 or 2-3030 running v.2.7.1 thru v.2.11.4 LCM code and programmed for alarm verification may not properly report alarm

v.2.17.1 LCM code released 04/05

Anomoly may cause Acclimate smoke programmed for alarm verification to not report alarm if the following conditions are present

Acclimate detector is programmed for alarm verification

Alarm level reported doesn’t change for verification period

Smoke and/or heat levels remain the same for entire period

Smoke detector portion caused the initial verification & heat portion does not activate during confirmation period

No other device activated during entire verification period

If alarm level changes during confirmation period an alarm will be reported

Detectors NOT programmed for alarm verification will not be affected

LCM v.2.16.3 corrects issue

Label on LCM EEPROM in lower left corner of board marked U22

All systems using v.2.7.1 thru 2.11.4, LCM code should be upgraded

TB07-04-01	STANDOFF INSTALLATION

Standoffs for LEM-320 behind LCM-320 can be installed in wrong location

Standoffs mounted in middle 4 holes

ENCLOSURES

CAB-4, AUDIO DRESS DOORS, EQ EQUIP, BATTERY BOXES

CAB-4 SERIES

ONYX CABINETS (BACKBOX/DOOR)

BACKBOXES FEATURE:

One to four rows for mounting CPU, CHASSIS, AMPS, ETC

Bottom row used for power supply & batteries

CAB-4 – NFS-320SYS, NFS2-640, NFS2-3030

NFS-320 has its own cabinet

SBB – A4		SBB ->SURFACE BACK BOX

A -> # OF EQUIPMENT ROWS (A=1, B=2....)

4 -> CAB 4 SERIES

DOORS

DR-A4-B R		DR -> DOOR

A -> # OF EQUIPMENT ROWS (A=1, B=2....)

4 -> CAB 4

B -> STYLE B blank door, nothing means Windows

R -> RED, nothing means Black

AUDIO DRESS DOORS

ADDR-B4 B R		ADDR ->AUDIO DRESS DOOR

A -> # OF EQUIPMENT ROWS (A=1, B=2....)

4 -> CAB 4

B -> STYLE B blank door

R -> RED, nothing means Black

EQ CABINETS

Equipment blank mesh doors

Same dimensions as CAB-4

Eliminates space for rows

Back box and door available in B,C,D sizes w/ optional trim ring

CAB-4 hinges mounting – ATTACH BEFORE EQUIPMENT INSTALLED IN CABINET

Lock must installed in lock position when key removed

INTELLIGENT DETECTORS

B224RB RELAY BASE – ONE FORM C relay for control of auxillary functions ie. Door release, etc.

2 modes – 	SHORT delay – JP1 (1&2) 60-100ms

LONG delay – JP1 (2&3) 6-10 seconds

N/O or N/C

FAPT-851 ACCLIMATE PHOTO/THERMAL detector

Multi-criteria smoke using photo & thermal to increase immunity to false alarms

Internal microprocessor adjusts sensitivity based on environment without programming

Photo sensitivity to smoke increases when rise in heat is sensed.

Capable of heat only mode, enabled by special command from panel.

FSB-200 (S)

Addressable beam detector

Transmitter, receiver, reflector protection range is 16 to 318 feet

Built in isolators

Style 7 operation

FSB-200S

Integrated sensitivity test feature in the way of filter attached to servometer inside optics

Activation of remote test station rotates filter into pathway of light beam (RTS451)

Quick & easy test without accessing device

Servometer needs 24VDC external source

Installation includes completion of coarse and fine alignment procedures,	        (I56-2544-004R):

Coarse alignment

Fine alignment

Final gain adjustment

Final verification

Specs, wiring, pre-alignment, coarse adjust, fine adjust, final gain, final vi, short circuit isolation, sensitivity selection, reflector test card procedure

D SERIES DUCT SMOKES

DNR – 	samples air current passing thru duct

Fan shutdown, etc

Low flow technology detects at air speed velocities of 100 to 4000 FPM

Pivoting housing

Remote alarm LED (RA400Z)

Remote test RTS451/RTS451KEY

DNRW-	NEMA 4 rating

Watertight enclosure

Not substitute for open area smokes

Not substitute for early warning

Not replacement for regular fire detection system

Tamper signal when cover removed

Standard smoke head (separate)

Cover isolates head from low flow feature for simple maintenance

2 wire loop for connection to smoke and optional relay or control module

Remote test device requires additional 2 wire for power

D SERIES

D2- 2 wire conventional

D4120 – 4 wire conventional

D4120W – 4 wire conventional watertight

DNR – Intelligent, non relay

DNRW Intelligent non-relay, watertight

FSC-851 – INTELLIQUAD MULTI-CRITERIA

4 sensing technologies that work together

Photo, thermal, carbon monoxide, infrared

DOES NOT generate 4 separate signals

ADDRESSABLE MONITOR MODULES

Interface to conventional circuits

Retrofits

Interface to N/O contact alarm devices

Two wire smokes

Non-alarm devices

Manual pull stations

New style H TYPE, same model #, new features

Terminal labelling on the side, Side mounted terminals for easy installation, Re-oriented address switches

Some modules require 24VDC (T11/T10)

Conventional circuits (T8/T9)

Loop connections (T1/T2)

FMM-1 	MONITOR MODULE

Used to monitor a zone

Wired as Class B (Style B) or Class A (Style D)

47kohm EOL

No resistor required for Style D

Max IDC loop length is 2500 ft

N/O, dry contact, alarm

4 wire smokes, pulls, flows, SV, heats, non-alarm contact types

By assigning certain software type Ids, normally open supervisory devices may be monitored with special SV indication at the panel.

FDM-1 	DUAL MONITOR MODULE

MONITORS 2 Class B/Style B dry contact IDC at 2 separate, consecutive addresses

Can be used to monitor a zone of 4 wire smokes, pull, flow, & N/O dry contact

By assigning certain software type Ids, normally open supervisory devices may be monitored with special SV indication at the panel.

Ideal for monitoring flow and tamper SV at same module

XP10-M		MONITOR CARD

Provides multiple circuit interface to same devices as FMM-1

Supports up to 10 Class B(Style B) or 5 Class A(Style D) circuits

Initial address is set from 01 to 150 and remaining modules assume the next 9 addresses

Panel controlled LEDs (green)

Panel can cause LEDs to blink, latch ON or latch OFF

47k EOL

Any # of devices on circuit as long as it doesn’t exceed 1500 ohms

Module must be powered down to make changes to shunts

DO NOT set base above 150

NEVER mix alarm and tamper devices on same circuit.

To Configure:

For Class A(Style D), remove A/B SLCT shunt

When Class A(Style D), alternate circuits are paired together & addresses are 2,4,6 or 8.

With A/B SLCT shunt in place, module is configured for 10 Class B(Style B) circuits 0-9

It is possible to disable ONE or TWO circuits in Class B or ONE circuit in CLASS A by installing a shunt in DISABLE 1 or DISABLE 2 positions of J1

Modules disabled from highest downward

Can be configured to send signal to NFS-320 or NFS2-640 to activate on board NAC circuits & alarm relay in event of failure of panel’s CPU – Jump CL of J1 enables feature

Degraded Mode

If system enter degraded mode due to failure of CPU:

NFS-320/2-640: General Alarm

Initiation of any inputs puts panel in full GA

NFS2-3030: per each SLC loop, alarm on any input on that loop puts panel in full GA.

FZM-1		FLASHSCAN ZONE MODULE

Used to monitor & supervise a zone of 2 wire, 24VDC smokes on Class A or Class B

Requires separate 24VDC power to power 2 wire detectors

Supervises connection of the power

XP6-MA	SIX ZONE MONITOR MODULE

Interface between ONYX and conventional 2 wire smoke detection zones

Common SLC input used for all modules and share common external supervisory supply and ground. Otherwise, they operate individually

Transmits status of zone and supervises zone of detectors and connection of external power supply

Initial address is set from 01 to 154 and remaining modules assume the next 9 addresses

Panel controlled LEDs (green)

Panel can cause LEDs to blink, latch ON or latch OFF

It is possible to disable ONE or TWO circuits in Class B or ONE circuit in CLASS A by installing a shunt in DISABLE 1 or DISABLE 2 positions of J1

Modules disabled from highest downward

Must be powered down to change shunts

DO NOT set base above 154

SHOWN CONFIGURED FOR 3 CLASS A(STYLE D) CKTS WITH ONE CIRCUIT DISABLED

To configure for 3 Class circuits, REMOVE BOTH A/B SELECT shunts

Alternate circuits paired together

Other addresses available for other devices

With A/B SHUNT in place, configured for 6 Class B circuits

Consecutive range of addresses to base address +5

3.9k EOL

2 wire detectors must be listed w/XP6-MA

FMM-4-20 	ANALOG INPUT MODULE

Translates 4-20mA signal from 2 or 3 wire sensors and communicates in flashscan

Provides unique non-alarm signal under UL NM listing

Requires 24VDC power supplied to power circuit

Supervises power

Transmits status of sensor (normal, open, alarm) to panel

4mA = 0% signal, 20mA = 100% signal

4mA as 0% allows panel to distinguish between zero signal and open circuits

Allows low powered devices to be directly powered by loop

Developed in 1950s

Only one sensor can be connected to the module

28 – 30 – 32 – 34 – 36

64 – 66 – 68 – 70 - 72

User programmed for up to 5 event thresholds, based on concentration level of gas being monitored

Executes appropriate pre-programmed response

Can be labelled as any: Fire, security, non-fire trouble, pre-alarm, non-fire & critical process

ADDRESSABLE CONTROL MODULES

Redesigned like monitor modules H TYPE

FCM-1	CONTROL MODULE

Notification appliances

Monitor telephone circuits

Activated manually or thru programming

Supports 2A of resistive load

1A of inductive load (mechanical bells or horns)

Can be wired Class A or Class B NACs

Size NAC using voltage drop calc software

47k EOL

Power supervision relay required at end of 24VDC power run

Except if last device on power run is a flashscan module using Type ID that provides built in power supervision

Supports speaker circuits Class A or Class B

Class B – 47k EOL

Class A – 100uf non polarized capacitors are required across terminals 6&9, 7&8

Audio circuit wiring must be twisted pair as minimum

Speakers must be listed for fire protection

Can be used to replace the U Type FCM-1 module in existing fire phone applications

When used for fire phones,

Remove jumper J1, located on back cover of module

MODULE BARRIER

Used in non power limited applications

CB500 module barrier used to separate power limited and non power limited terminals

Must be used in 4x4 box

Power limited wiring placed in isolated side of barrier

XP6-C	MULTI CIRCUIT NAC MODULE

Provides 6 supervised Class B/Style Y, or 3 Class A/Style Z circuits for control of NACs

Also used for fire phones

External power must be supplied on command from panel

XP6-C disconnects supervision& connects external power supply across the load devices

Initial address is set 01 to 154, remaining assume next 5 addresses

With A/B SHUNT in place, configured for 6 Class B circuits

With A/B SHUNT removed, configured for 3 Class A circuits

Alternate circuits paired together

Addressed 0,2,4....

Ie. Module set to 28, Style Z – 28,30,32, 29,31,33 available for other devices

It is possible to disable ONE or TWO circuits in Class B or ONE circuit in CLASS A by installing a shunt in DISABLE 1 or DISABLE 2 positions of J1. Extra addresses freed up for other devices

Modules disabled from highest downward

Must be powered down to change shunts

# of modules disabled is affected by A/B Shunt

If configured for Style Z and shunt is installed across DISABLE 1, 3 addresses available under Class A, module would use 2 addresses

Short circuit protection can be enabled to protect external power supplies from shorts on NACs.

Enable short circuit protection when a single power supply is shared by multiple NACs. Short circuit protection can be disabled only when a power supply is not shared by multiple NACs.

There is an active short circuit protection option for each address. The board is shipped with this option disabled for each address represented by six large shunts on the “Disable Short Circuit Protection” area. To enable short circuit protection for an address, remove the corresponding

shunts on the “Disable Short Protection” area. When enabled, this option will isolate a short occurring on any active circuit allowing the remaining circuits to continue normal operation.

NOTE: Power supply monitoring should not be used for audio

applications. The short circuit protection feature is also

not available for audio applications.

NOTE: The XP6-C does not provide ring back when used as a firefighter telephone circuit.

NOTE: Short circuit protection may only be enabled if power supply monitoring is enabled.

NOTE: This feature is not for use with all Fire Alarm Control

Panels. Please consult with Technical Services before

enabling this feature.

NOTE: Place unused shunts on single pin to store on board for

future use.

NOTE: Power must not be applied to the unit when changing functionality of

the shunts.

NOTE: Whether in Class B or Class A wiring, power supply monitoring and

short circuit protection must be enabled on the NAC circuits that are sharing

a power supply.

NOTE: Short circuit protection can only be disabled if a power supply is not

being shared by multiple NACs.

SYNCHRONIZATION

SYNC-1 	SYNC CARD

Works with System Sensor SpectrAlert & SpectrAlertAdvance series to provide means of sync’n temporal coded horns and timing of strobe flashing

Enables silencing of horns in horn/strobe combos over 2 wire circuit while leaving strobes active

Capable of syncing 6 Class B or 3 Class A circuits

Multi circuit NAC module

Each set of 6 Class B are wired to term block with 47k EOL

Each of 3 Class A share 2 terminal blocks

XP6-C has provision for connection of external power source if source desired

All NACs can be wired powered by separate external supplies or a single supply can be shared among multiple NACs

FRM-1	RELAY MODULE

Dry contact outputs for activating auxiliary devices

Form C

2 sets of contact switch together (DPDT) are rated for 2A resistive or 1A inductive or 0.5A Pilot duty(?)

Activated manually or thru panel

DOES NOT supervise controlled circuits

XP6-R	RELAY CARD

6 separately addressed Form C relays

Single isolated set of dry contacts provided for each module. N/O or N/C

Addressed 01 to 154

With A/B SHUNT in place, configured for 6 Class B circuits

With A/B SHUNT removed, configured for 3 Class A circuits

Alternate circuits paired together

Addressed 0,2,4....

Ie. Module set to 28, Style Z – 28,30,32, 29,31,33 available for other devices

It is possible to disable ONE or TWO circuits in Class B or ONE circuit in CLASS A by installing a shunt in DISABLE 1 or DISABLE 2 positions of J1. Extra addresses freed up for other devices

Modules disabled from highest downward

Must be powered down to change shunts

# of modules disabled is affected by A/B Shunt

FCM-1-REL	RELEASING MODULE

Provides additional safeguards & features specifically designed for suppression releasing

Power for release solenoids runs thru module for full time supervision ensuring minimum voltage to activate

In Style D (Class A) configuration, device will monitor solenoid, even in event of short circuit

NO EOL required

ONE 24VDC or 2 12VDC solenoids per circuit

REQUIRED for all NEW flashscan mode releasing applications with

NFS2-3030(V14+)

NFS2-640 (V12+)

NFS-320 (V12+)

Use FCM-1 for rfeleasing applications on NFS-640, 3030, and ALL CLIP mode panels

When using FCM-1-REL in Class A, remove J1 (inside module)

REDUNDANT PROTOCOL

Minimizes likelihood of unintentional release.

MUST be armed first with pair of signals

Enters 3 second window awaiting pair of signals

If no confirmation, module will auto-reset

MODULE MOUNTING

4X4 box

Supplied with plastic cover

Notifier offers SMB500 surface mount box

CB500 Module barrier

MODULE CARD MOUNTING

BB-XP Cabinet

One or 2 modules

Internal chassis with offset mounting

CHS-6 chassis supports mounting of up to 6 multi circuit cards

BB-25 back box

Holds one CHS-6

CAB-4 enclosure

Holds up to 4 CHS-6

Module cards can be mounted in separate enclosure when used with NFS-320, or inside cabinet on 2-640/2-3030

SMOKE CONTROL MODULES

SCS-8 – smoke control station

SCE-8 – smoke control expander

Provides ONYX with capability to control & display status of AHU fans and dampers

MAX configuration of 32 pairs, system capability to control & display status of up to 512 separate fans/dampers

ADDRESS 1                             ADDRESS 2                           ADDRESS 3

SCS-8

2 modes of operation:

Fire fighters smoke control station (FSCS)

HVAC

FSCS (2-3030 & NCA-2 ONLY)

Helps maintain and enable environment in evacuation routes during time required to evacuate people from areas

Helps restrict movement of smoke from fire area

Helps provide conditions in non-smoke areas that will help fire officials conduct search and rescue

SCS intended to have highest priority over associated fan & damper functions.

REQUIRES CONTROL AND VERIFICATION OF A PARTICULAR DEVICE

NFS-2-640 can only be used if connected to NCA-2 network annunciator

Capability doesn’t exist when NCA-2is being used as primary display for NFS2-640 (Not functioning as network display)

HVAC Mode

Capable of monitoring and controlling both HVAC, either separately or by overriding normal building usage

When used for smoke control, HVAC can:

Supply outside air to a space

Return air to a space

Exhaust air from a space to outside

HVAC DOES NOT require control and verification of a particular device

HVAC mode is not consistent with UL & NFPA standards for smoke control. This mode should be used for fan shutdown and building HVAC and A/C purposes only.

SWITCH GROUPS

SCS/SCE-8 has 8 switch groups, each with 2 LEDs and 1 switch

Each annunciator has ACK switch which is also Lamp Test

Green LED means all working in automatic mode

If any switches moved, AMBER ‘Manual’ LED lights

Each fan/damper has one switch group on SCS/SCE

Each group has up to 4 points that could be used to control a fan/damper

FAN ON (Damper Open)

FAN OFF (Damper Closed)

MONITOR/VERIFY FAN ON/DAMPER OPEN

MONITOR/VERIFY FAN OFF/DAMPER CLOSED

If fan/damper requires ALL 4, then 2 control modules must be connected to the device & ONE point would be for each of the 4 functions

AUTO – alarm on panel, module will function per programming

OPEN/ON – overrides auto programming procedure, leaving it in OPEN/ON position

CLOSED/OFF - overrides auto programming procedure, leaving it in CLOSED/OFF position

Modules can be mounted inside CAB-4 using ADP-4 annunciator dress plate. Each plate can hold up to 4 modules & uses 1 row in the cabinet

Can also be mounted in ABS-4D annunciator surface box

ALL SCS/SCE modules configured for FSCS mode MUST be installed in same room as FACP of NCA to which they are connected.

INSTALLATION

Subject to same requirements as ACS annunciators

Filtered, regulated 24VDC power supplied to each module

Connection between SCS & SCE with ribbon cable

SCS DOCUMENTATION (DOC#15712)

CONON/OP – CONtrol module used to turn ON a fan or OPEN a damper

CONOFF/CL – CONtrol module used to turn OFF a fan or CLOSE a damper

VERON/OP – VERify  ON  fan or OPEN damper

VEROFF/CL – VERify  OFF  fan or CLOSED damper

VERIFICATION

Monitor ON/OFF state of a fan or OPEN/CLOSED state of damper

Contacts connected to sail switch determine if module is to monitor ON/OPEN or OFF/CLOSED

Verify ON state (N/O contact) T7/T8

Verify OFF state (N/C contact) T7/T8

Normally, addressable control modules are used to activate & deactivate NACs

When used with smoke control, they control ON/OFF, OPEN/CLOSED

CONTROL/VERIFICATION

Ie. FCM-1 wired to break power to fan upon activation (CONTROL OFF)

Once fan is turned off, FMM-1 is activated by change in state of fan’s switch (CONTACT CLOSE)

VERIFY OFF

TYPE COMBINATIONS

SCS/SCE-8 can be configured for a number of switch group type combos

9 different group types for SCS operating in non-dedicated FCSC mode (non alarm)

15 HVAC types:

Table 3.6 FSCS toggle switch (non alarm condition)

Table 3.7 FSCS toggle switch (alarm condition)

Table 3.8 FSCS toggle switch (LED operation)

Table 3.11 HVAC toggle switch function

Table 3.6 HVAC toggle switch group LED operation

DIP SWITCH SETTINGS

SEE MANUAL, PAGE 63

FSCS MODE DIP SWITCH SETTINGS TABLE 3.5 ON P. 64

HVAC DIP SWITCH SETTINGS TABLE 3.10 ON P. 77

PROGRAMMING

SCS special EIA-485 control annunciators

Points must be mapped to control module & monitor module assigned to each switch group

First, define required addresses as FSCS or HVAC

SLC can support up to 32 addresses for ACS, SCS, LDM annunciators & UDACT digital communicators

Each address supports up to 64 points on NFS-320 or NFS2-640

Each address supports up to 96 points on NFS2-3030 or NCA-2 BUT each point MUST be programmed, whether used or not.

POINT: Point 1 or 64 (or 96)

MODE: Control for a control module

SOURCE: SLC loop address of control module

RELAY MODULE: Control

CONTROL MODULE: Control

MONITOR MODULE: Verify

SCS-8L/SCE-8L	SMOKE CONTROL LAMP DRIVER/EXPANDER

Designed to interface with custom graphic annunciator

Each SCS-8L has capability to CONTROL and MONITOR 8 AHU fans or dampers

Can operate in FSCS or HVAC

Max config of 32 pairs

Can control and display status of up to 512 separate AHU fans or dampers

Addresses come from pool of 32 ACS addresses available to single ONYX control panel

SCS-8L INSTALLATION

Groups 1 - 4 – J3

Groups 5 – 8 – J4

SLC – TB2

Power – TB1

SCS-8L/SCE-8L INSTALLATION – PAGE 49

CHS-4L INSTALLATION - PAGE 48

WIRING SWITCHES – PAGE 54

INSTALLING RELAY MODULES – PAGE 54

PROGRAMMMING BASICS

TYPE CODES

Software selections for SLC loop devices

Apply to 3 basic categories of SLC devices:

Detector, monitor, control

TYPE IDs

Do not actually change manner in which device operates

Codes define how control panel is to respond to activation of input device or control functioning of an output device

5 basic threat categories

Alarm, supervisory, security, trouble, other event (2-3030 only)

Codes further define whether a device change in status should be latch or tracked by a point.

MONITOR: LATCHING fire alarm signal

NON-FIRE: MONITOR non-fire alarm devices

PULL STATION: LATCHING without alarm verification

WATERFLOW: LATCHING waterflow

SPRINKLER SYS: NON-LATCHING without verification

DRILLS WITCH: EVAC from remote location

ABORT SWITCH: NON-ALARM abort function

NFS-320/NFS2-640 contain 4 onboard convention NACs which can be programmed with certain codes:

CONTROL

STROBE CKT

HORN CKT

SPEAKER

RELEASE CKT

ALARMS PENDING

NFS2-3030 programming manual contains TYPE CODES Appendix – PAGE 138

BOOLEAN LOGIC

Logic gates. AND, OR, NOT......

Used alone or in combinations

Series or parallel is used to control precedence of operations

OR

Logical disjunction

Results in a TRUE state for output whenever ONE of the inputs is TRUE

AND

Both inputs TRUE

NOT

Output is inverted of input

VENN DIAGRAM

|  | Graphically represents the results of combining basic Boolean operators |
| --- | --- |

XOR

Onyx system’s XOR is called ONLY1

Can be used to GATE activation of a releasing mechanism with an abort switch

If pulled within certain period of time following activation of a detector, switch aborts the pending activation of the releasing device. EXAMPLE ONLY, LOGIC NOT NEEDED IN ONYX.

SOFTWARE EQUATIONS

Written to define relationships between inputs and output devices

Equations help convert human language into format understood by panel

If this detector or this pull is activated, turn on these strobes

LOW (0) – NORMAL, NOT ACTIVATED

HIGH (1) – ALARM, ACTIVATED

OR(L1D01,L1M03)

CBE	CONTROL BY EVENT

Method of controlling outputs by activation of specific inputs

Finite limit to # of elements that can be in CBE equation

Software zone can be used to accomplish same programming objective with less effort

LOGIC ZONES

General zones used as an arguement in logic equations, implemented using logic zones

ONYX systems also offer Trouble zones (2-3030), Releasing zones & Special zones

Logic zones defined by logic equations which is CBE equation that employs a logic function

Whenever logic equation becomes TRUE, all outputs mapped to that logic zone will activate.

Logic zone can then be programmed into zone map for each device intended to control

NFS-320 & NHS2-640 have capability of 20 logic zones, ZL1-ZL20

NFS2-3030 has capability of 1000 logic zones, ZL1-ZL1000

KDM-R2 – 80 character display shows E0 to E9 for logic zones 1-10 & L0 to L9 for 11-20

Once logic zone has been added to zone map for an output device, we have CBE solution

TROUBLE ZONES

Defined by equation with logic

When trouble equation becomes true, all outputs mapped will activate

Trouble zone is programmed into zone map for each output device intended to control

NFS-320/NFS2-640 DO NOT HAVE TROUBLE ZONES

NFS2-3030 HAS 100 TROUBLE ZONES, ZT1-ZT100

NFS2-3030 programming manual has system troubles appendix on PAGE 144

RELEASING ZONES

USED TO CONTROL RELEASING OPERATIONS

NFS-320/NFS2-640 have 10 releasing zones, R0-R9

NFS2-3030 has 10 10 releasing zones, R0-R9

DELAY TIME – 60 seconds

SOAK TIME -  defines length of time to dump releasing agent on activation.

0= active until reset

DO NOT USE SOFTWARE DISABLES FUNCTIONS AS LOCKOUT

NFS-320/NFS2-640 – DO NOT ENABLE BACKUP OPTION SWITCH FOR ANY OF THE NACs IF USED FOR RELEASING

NFS-320/NFS2-640 – Limit of 73 characters including (,) & commas

NFS2-3030 – 80 characters

Limit of 20 arguements with 10 functions (or one time delay)

LOGICAL CONJUNCTION

2 place logical operation that results in a value of TRUE if both of its operands are true, otherwise value is false

EXCLUSIVE CONJUNCTION

Type of logical disjunction on two operands that results in a value of TRUE if AND only if exactly one of the operands is true

XOR = when more than 2 inputs are used, a HIGH OUTPUT results when there are and ODD # of TRUES (See ONLY1, only one input has t be true

IP COMMUNICATOR

Use existing IP networks (LAN, WAN) & internet connections to transmit alarms

Eliminates cost of phone lines

Increased supervision from once a day to every 30-90 seconds

No change to existing panel configuration, connects directly to panel’s dialer outputs

Works over any type of Ethernet 10/100 base T

DHCP or static IP

Less than 10 second alarm transmission line

Auto register can be pre-configured offsite

Can connect to primary and secondary output of panel’s DACT

Optionally, Secondary DACT can be connected to phone line if required

Communicates contact ID info to compatible TELDAT receiver via internet

UL-864 9th edition listed for signalling type “OT” other transmission technologies

PSDN(?) for both proprietary & commercial central stations

Listing meets all requirements for a single communications line under NFPA72

ANY FAILURE annunciated at supervising station WITHIN 5 MINUTES

If communication failure with supervising station, indicates at panel

If portion of communication path can’t be monitored, redundant communication path shall be provided

Failure of both primary and redundant communication paths shall be shown at supervising station within 24 HOURS. USUALLY DONE WITHIN 90 SECONDS

System units at supervising station shall be restored to service within 30 minutes if failure

IP Communicator simulates standard PSTN analog line

During event, it senses off hook status, counts digits of the dialed phone number, then begins collecting CONTACT ID data

FRAMES the CONTACT ID data using UDP packets (UDP instead of TCP/IP when very small amounts of data need to be sent) with 512bit AES

Receiver decrypts & unpackets data and sends ASCII data to software

Automation software or receiver can provide the “kiss-off” signal to panel

Communicator ships with:

30” telephone cable

2 ferrite rings

2 1k ohm resistors

Manuals/cd

Quick programming guide

P1 – RESET JUMPER – when jumped, will return to factory defaults on power up

TO AP – provides simulated phone line transmission to DACT

Enabled only after IP communicator initially registers with control station receiver

Failure of communication path to receiver will result in disabling this connection – TELCO fault on panel

12V or 24VDC filtered, regulated power

Polarity reverse will damage unit

RJ45 ethernet connector – 10/100 Base T

LEDs	1-power on

2-UDP polling, LED goes out when acknowledgement received, blinking-ready to auto register

3-light when alarm panel seizes phone line, waits for correct # of digits. LED out when acknowledgement received

4-when IP packet of alarm info is sent out. LED out when acknowledgement received

5-bit-directional maint call has been made with alarm panel

6-IP communicator has intercepted phone line & has activated phone relays

MOUNTING

Mounted in separate enclosure P/N-IP-ENC (red or black)

Can be mounted in an HP3000LX power supply

Can draw as much as 98mA in alarm. If panel can’t handle it, the HP3000LX power supply can be used

PPBRKT (bracket) can be installed inside power supply cabinet

PHONE LINE CONNECTION

- Loop supplied phone cable thru larger ferrite rings twice

- Connect bare ends of cable to terminals ‘TO AP’ or IP communicator

- Plug in phone cable’s RJ45 connector into IPSPLT splitter (separate)

- Connect the two 9” flat phone cables supplied with IPSPLT to primary and secondary  dialer outputs.

    - If panel’s DACT doesn’t have RJ45 connectors, simply make 2-wire connections from IP communicator’s ‘TO AP’ to both primary and secondary DACT outputs

Phone line polarity is not polarity sensitive

POWER CONNECTION

- Loop cable thu small ferrite ring twice

- Connect to + & -

NETWORK CONNECTION

Plug straight thru CAT5 cable into IP communicator

Plug other end into router

If pre-programmed, will register in a few seconds

Maximum distance is 328 feet (100 meters)

PROGRAMMING

Serial connection or Ethernet connection

Windows PC

9 pin serial com port (requires p/n ALMSC119)

USB to serial converter

Network interface card

ETHERNET CONNECTION

Using network hub with straight thru cables

Or CAT 5 crossover patch cable

IDACT CONFIGURATOR

Windows based

Can use hyperterminal or other serial communication software

Your choice using Ethernet or serial

TELNET programming, has browser function that queries connection

Auto register feature

PROGRAMMING VIA TELNET

Need static IP address on PC in same IP scheme as IP communicator’s default address (192.168.0.100)

Use IP address 192.168.0.XXX (any number between 1-255 except 100)

QUICK INSTALL

Before programming, get all info from central station’s IT dept.

Customer decides DCHP or static IP address

If STATIC, box must be unchecked

Password is required to initially register w/ central station receiver before it can send events

Onsite: results in registration as part of the configuration process when configure button pressed

Offsite: when registration password and complete config process by checking configure button

LED2 will flash. Will auto register when connected.

WEBINAR

VERIFIRE TOOLS

NEW FEATURES

NETWORK DIAGNOSTICS

See panel & software versions

Test network

Port statistics

HELP

Website, product improvement

NFS2-640

Relay configuration

DRILL MODE:	STANDARD

CUSTOM (associate zone to participate in DRILL)

FB = F16

F10 = alarm verification

F8 = BELL CODE (connected to 2-640)

New options

NETWORK MAPPING

| SOUNDER BASE – NEW BASE B200S HIGH – 86Db Low – 75Db MODULES – NO CHANGES BELL CIRCUITS – NO CHANGES | GENERAL ZONES – SILENCEABLE CHECK BOX NEW VALIDATION – cause & effect SIMULATOR – now can print per each device |
| --- | --- |

NFS2-3030

Adding new node # that already exists will overwrite old one.

Shows node and panel type in toolbar in network mode

GENERAL 1 – NO CHANGE

GENERAL 2 – DRILL MODE added

F16 – DRILL MODE OUTPUT

GENERAL 3 – NO CHANGE

GENERAL 4 – NO CHANGE

GENERAL 5 – 	override daylight savings time

Sounder base settings

B200S base

Custom tones – new

Temporal, 3 on 3 off, 0.5 seconds

Period ON time and OFF time

Tone OFF period – 1.5s

Pulse ON time – 6 seconds MAX

Period – 6 seconds MAX

`	Number of pulses – 255 pulses MAX

ALL SOUNDERS GO ON THIS SETUP

SLC LOOPS – NO CHANGE

OCCUPANCY SCHEDULE – NO CHANGE

ACS MAPPING – NO CHANGE

ACS POINTS – NO CHANGE

REMOTE DISPLAY – 	LOCAL CONTROL

Allows control on display

NETWORK MAPPING - 	only active if node is not node 0

Click NETWORK DISPLAY MODE

Current node checked  & greyed out

NFS2-3030 CAN BE USED AS NCA ON NETWORK

Will perform function of NCA if boxes checked as long as its one other panel, not legacy

Up to 4 DVC

Can also setup in large network that can take care of certain sections of network

LIMIT OF 25

POINT PROGRAMMING

DETECTOR – intelligent sounder base options

CUSTOM – global setup in SOUNDER BASE section

MODULES – FMM-4-20 MONITOR MODULE

Works with 4-20mA devices, gas detection, etc

Setup thresholds

CBE – 3,4,5,6,7 – BLUE – means special addition function

00 = 320F

1000 = boiling

Ie. 	4mA scale 0o = low limit

20mA scale 100o = upper limit

Units = DegC

Hysterisis = 2% (+/-2oC) Response lag

Thresholds button – plug in values for the CBE

Ie

|  | VALUE | EVENT | TRIGGER | TYPE |
| --- | --- | --- | --- | --- |
| CB3 | 10O | NON-FIRE TROUBLE | LOWER LIMIT | TROUBLE 1 |
| CB4 | 20O | CRITICAL PROCESS | UP |  |
| CB5 | 15O | NON-FIRE ACTIVATION | SPECIFIC LEVEL |  |
| CB6 |  |  |  |  |
| CB7 |  |  |  |  |

CLICK MODULE THEN PUT IN THE CBE ZONES TO ACTIVATE ON THESE CONDITIONS

CRITICAL PROCESS TAKES PRIORITY

GENERAL ZONES - 	GENERAL ALARM – ZONE 0

Can make zones silenceable

Can make zones re-settable

RELEASING ZONES - 	NO CHANGE

MODULE THRESHOLDS- 4-20Ma MODULE SETUPS

LOGIC EQUATION BUILDER SERVICE

New features – FIRE, PREALARM, DIS, SUP, SEC

(primarily put in for the 4-20mA module)

SMOKE CONTROL

System programming

ACS MAPPING – FSCS

ACS POINTS – TYPE FSCS

FSCS – 96 POINTS		(SCS-8 WITH TOGGLES)

HVAC – 1-64 POINTS

NFS2-640 - SCS-8 ONLY USED IN HVAC MODE

NFS2-3030/NCA – 96 POINT ANNUNCIATOR

1ST FIRE ALARM, DAMPERS ACTIVATED, THEN LOCKED OUT. ALL OTHER ZONES CAN BE MANUALLY USED

SCS-8/SCE-8 TOTAL OF 32 POINTS

8 SWITCHES, 2 CONTROL/2 MONITOR PER SWITCH (64 POINTS TOTAL)

NFS2-3030 - POINTS 65 TO 96 & install programming to make true FSCS operation

NFS2-640 – If networked 2-640s and you have NCA, use ACS bus on NCA

Or setup one 2-640 with NCA to use ACS bus

65-96 monitor points to use FSCS

Monitor module for unused points