Design Example

1. Sedimentation Tank: 

A conventional sedimentation tank is designed to treat raw water containing flocculent particle with settling velocity of about 0.5 m/h. The detention time is around 4 hours. The tank is a rectangular basin with length-to-width ratio: 3 to 1. The flow rate is 100 L/s. Density of water,  = 998 kg/m3, dynamic viscosity,  = 1.002 x 10-3 N-s/m2, kinematics viscosity,  = 1.004 x 10-6 m2/s, (water temperature is 20 oC), gravitational acceleration, g = 9.8 m/s2.

Determine:

1. The dimension of the sedimentation tank

2. The turbulence of flow in the sedimentation tank

3. The stability of flow during sedimentation

4. Instead of rectangular conventional sedimentation tank, tube settler will be applied to the same raw water as above. Compare both of sedimentation tank in respect to its dimension, turbulence of flow, and its stability. The height of tube settler, H = 1.2 m, width of tube, w = 5 cm,  inclined at  = 60o.

Solution:

Conventional rectangular sedimentation tank

vo = 
[image: image28.wmf]

[image: image2.wmf]60

*

60

5

.

0

= 
[image: image3.wmf]A

100

.

0

  or  A = 720 m2
Volume of sedimentation tank, V = Q t

V = 0.100 * 4 * 60 * 60

V = 1440 m3
V = A * h

1440 = 720 * h

depth of sedimentation, h = 2 m

A = 3w * w

720 = 3 w2
width of sedimentation tank, w = 15.5

length of sedimentation tank, L = 46.5

Dimension of the tank: 
L = 46.5 m






w = 15.5 m






h = 2 m 

vf = 
[image: image4.wmf]Ac

Q

= 
[image: image5.wmf]5

.

15

*

2

100

.

0

= 0.003226 m/s

Reynolds Number R = 
[image: image6.wmf]m

r

o

f

R

v

; Ro (hydraulic radius) = 
[image: image7.wmf])

2

(

w

h

wh

+


Ro = 15.5 * 2 / (2*2 + 15.5) = 1.6 m

R = 
[image: image8.wmf]3

10

002

.

1

6

.

1

*

003226

.

0

*

998

-

x


R = 5140 (R > 2000, turbulence flow) does not meet criteria for sedimentation

Froud Number, F = 
[image: image9.wmf]o

f

gR

v

2

= 
[image: image10.wmf]6

.

1

*

8

.

9

003226

.

0

2

= 0.00664x10-5
F < 10-5, unstable flow, does not meet criteria for sedimentation

Tube settler

vo = 
[image: image11.wmf]þ

ý

ü

î

í

ì

+

a

a

2

cos

cos

w

H

w

A

Q



[image: image12.wmf]þ

ý

ü

î

í

ì

+

=

60

cos

05

.

0

60

cos

2

.

1

05

.

0

100

.

0

60

*

60

5

.

0

2

A


A = 59 m2, the surface area of tube settler is much lesser than that of conventional sedimentation tank (A = 720 m2)

A = 3w * w

69 = 3 w2
width of sedimentation tank, w = 4.8 m

length of sedimentation tank, L = 14.4 m

Dimension of the tank: 
L = 14.4 m






w = 4.8  m






h = 1.2 m (height of tube settler)

vf = 
[image: image13.wmf]a

sin

A

Q

= 
[image: image14.wmf]60

sin

69

100

.

0

= 0.0017 m/s

Reynolds Number R = 
[image: image15.wmf]m

r

o

f

R

v

; Ro (hydraulic radius) = ¼ w

Ro = 0.25 * 0.05 = 0.0125 m

R = 
[image: image16.wmf]3

10

002

.

1

0125

.

0

*

0017

.

0

*

998

-

x

=21

R = 21 (R <<< 2000, laminar flow) satisfies criteria for sedimentation

Froud Number, F = 
[image: image17.wmf]o

f

gR

v

2

= 
[image: image18.wmf]0125

.

0

*

8

.

9

0017

.

0

2

= 2.34x10-5
F > 10-5, stable flow, satisfies criteria for sedimentation

2. Final Clarifier:

Batch settling test have been performed using an acclimated sludge from water treatment plant to give the data in Table 2.

Table 2: Concentration, settling velocities, and solids flux for various tests

	Test
	C (mg/L)
	V (m/h)
	G = CV (kg/h-m2)

	1
	12,460
	0.125
	1.56

	2
	9,930
	0.249
	2.47

	3
	7,450
	0.469
	3.46

	4
	5,220
	1.000
	5.22

	5
	3,140
	2.940
	9.24

	6
	1,580
	4.180
	6.60


The design mixed liquor flow to the final clarifier is 160 L/s, the MLSS is 2500 mg/L, and the underflow concentration is 12,000 mg/L. Determine the diameter of the final clarifier.

Solution:

The settling curve showing the settling velocity versus solids concentration is shown in Figure 16. From the data given in Table 2, the flux curve showing the solids flux versus solids concentration is shown in Figure 16. A tangent to the curve drawn from Cu = 12,000 mg/L gives a GL = 8.90 kg/h-m2. Using scale-up factor 1.5 (safety factor for design) will give GL =  8.90 / 1.5 = 5.93 kg/h-m2. The rate at which the solids settle (applied solids rate), Mt, is equal to Q0C0, or, QfCf
Mt = 
[image: image19.wmf]1440

1000000

2500

60

*

60

160

=

x

 kg/h

[image: image1.wmf]A

Q


The applied solids loading rate, 
[image: image20.wmf]L

f

f

G

A

Q

C

£



[image: image21.wmf]93

.

5

1440

£

A


A = 242.8 m2
Diameter of the tank, D = 17.6 m

3. Flotation

A wastewater flow of 1900 m3/day has 200 mg/L suspended solids. Air flotation tests show that 0.05 mg air/mg solids gives optimum flotation. The design temperature is 20 oC, and as = 18.7 mL/mL at this temperature. The fraction of absorption is 0.5, and the overflow rate is 117 m3/m2-d. Determine the required pressure and flotation tank area. If the operating pressure is 3 atm, determine the recycle ration and the flotation tank area.

Solution:


[image: image22.wmf]s

s

S

fP

a

S

A

)

1

(

3

.

1

-

=


0.05 = 
[image: image23.wmf]200

)

1

5

.

0

(

*

7

.

18

*

3

.

1

-

P


P = 2.82 atm


Plan area is:

A = 
[image: image24.wmf]2

.

16

117

1900

=

 m2

For a system where pressurized recycle is used, 


[image: image25.wmf]Q

S

R

fP

a

S

A

s

s

)

1

(

3

.

1

-

=


0.05 = 
[image: image26.wmf]Q

R

200

)

1

3

*

5

.

0

(

*

7

.

18

*

3

.

1

-


R/Q = 0.82

Plan area = 
[image: image27.wmf]117

)

82

.

0

1

(

*

1900

+

= 29.6 m2










































86
Web11-4; page 5

_1066733928.unknown

_1066736542.unknown

_1066806137.unknown

_1067684594.unknown

_1067701241.unknown

_1067703567.unknown

_1067703733.unknown

_1067701369.unknown

_1067685094.unknown

_1066806359.unknown

_1066737109.unknown

_1066740148.unknown

_1066736831.unknown

_1066734736.unknown

_1066735517.unknown

_1066736507.unknown

_1066735251.unknown

_1066734700.unknown

_1066724850.unknown

_1066725597.unknown

_1066724887.unknown

_1066725429.unknown

_1066723762.unknown

_1066723803.unknown

_1066723485.unknown

