Potential for Cogeneration in Ontario – Draft Report ( 2

Potential for Cogeneration

in Ontario

- Final Report -

Prepared for:

Ministry of Energy, Science and Technology
880 Bay Street, 3rd Floor

Toronto, Ontario

M7A 2C1

in Cooperation with 

Ministry of Natural Resources

Ministry of Economic Development and Trade
Prepared by:

Hagler Bailly Canada

4 King Street West, Suite 1310

Toronto, Ontario

M5H 1B6

In Association with

AGRA Monenco

Lourie and Love Environmental Management Consulting

HBIX Reference 788

August, 2000

11.
Introduction

1.1
Process for the Project
2
1.2
Contents of the Report
2
2.
Estimates of Cost of Cogeneration in Ontario
3
2.1
Assumptions
4
2.1.1
Gas Prices
4
2.1.2
Large and Medium Technologies
4
2.1.3
Small Technologies
5
2.2
Cost Estimates
6
2.2.1
Large and Medium Technologies
6
2.2.2
Estimated Costs for Small Cogeneration
11
2.3
Electricity Prices
14
3.
Technical Potential for Cogeneration in Ontario
16
3.1
Methodology and Data Sources
17
3.1.1
Large and Medium Cogeneration
17
3.1.2
Small Cogeneration Applications
17
3.2
Estimates of Technical Cogeneration Potential
18
3.2.1
Estimates for Industrial Applications
18
3.2.2
Technical Cogeneration Potential in Commercial and Institutional Applications
21
3.2.3
District Heating
23
3.2.4
Technical Cogeneration Potential in the Residential Sector
24
3.3
Total Technical Potential
24
4.
Economic Potential for Cogeneration in Ontario
26
4.1
Methodology
26
4.1.1
Large and Medium Scale
26
4.1.2
Small Scale Generation
27
4.2
Market Considerations
27
4.2.1
Electricity Prices
27
4.2.2
Capital Costs
29
4.2.3
Fuel Costs
29
4.2.4
Other Factors
29
4.2.5
Sensitivity Analysis
30
4.3
Cogeneration Potential: Base Case
31
4.3.1
Economic Potential for Large and Medium Scale
31
4.3.2
Economic Potential for Small Scale Cogeneration
34
4.3.3
Total Economic Cogeneration Installed Annually: Base Case
34
4.4
Cogeneration Potential: Alternate Cases
35
4.5
GHG Reductions Associated with Cogeneration
36
5.
Analysis of Barriers to Cogeneration
38
5.1
Market Barriers
39
5.1.1
Low Price for Electricity
39
5.1.2
Artificially Low Cost to Reactivate 5 GW Nuclear Capacity
40
5.1.3
Market Power of OPG
40
5.1.4
Market Rules
40
5.1.5
Standard Supply Service Code
41
5.1.6
Cost of Cogeneration Technology
41
5.1.7
Undervaluing of System Reliability
42
5.1.8
Cost of Back-up Electricity
42
5.2
Institutional Barriers
42
5.2.1
Reluctance to Make Long-Term Commitments
42
5.2.2
Competition for Limited Funds and Senior Management Attention
43
5.2.3
Attitudes of Senior Management
43
5.2.4
Lack of Information, Understanding and Confidence
43
5.2.5
Early Stage in Development of Industry of Facility Owner/Operators
44
5.2.6
Local Resistance to Siting of New Facilities
44
5.2.7
Transmission Infrastructure
45
5.2.8
Interconnection Requirements and Costs
45
5.2.9
Lags in Equipment Availability
45
5.3
Regulatory Barriers
46
5.3.1
Transmission and Distribution Pricing
46
5.3.2
Environmental Assessment and Approval
46
5.3.3
Assets Included in Class 43
46
5.3.4
Proposed Power Engineers Regulations
46
5.4
Barriers With No Apparent Policy Approaches
47
5.4.1
Uncertain Future Natural Gas and Electricity Prices
47
5.4.2
Availability of Steam/Low Grade Heat Hosts
47


Appendix A
Gas Price Report

Appendix B
First Workshop Report

Appendix C
Second Workshop Report

1. Introduction 

Cogeneration (the combined production of heat and power, where both products are utilized) can get the highest utilization of the energy available from a fuel, making it the most efficient way to generate electricity using fossil fuels. Substituting cogeneration for generation from more intensive emitting sources can reduce both greenhouse gases (GHGs) and other pollutants. Ontario is the third largest producer in Canada of electricity from coal, which is the most intense GHG emitter of the fuels used for electricity production. 

This project is intended to address the future prospects for cogeneration in the context of a restructured electricity market in Ontario. Its estimates of economic potential and its identification of the key factors affecting implementation will provide the Ontario government, and others, with information to use in tracking performance. Its identification of barriers will help the government to plan policies that can affect that performance.

The electricity supply industry in Ontario is being restructured from monopoly-based to competitive. The Ontario government has indicated that restructuring should not degrade the industry’s environmental performance; its White Paper listed “Enhanced safety, reliability and environmental protection” as goals of electricity restructuring.

One of the most important environmental impacts of electricity generation is the result of air emissions. Coal-fired electric stations are major emitters of SO2, NO, mercury, and CO2 as well as particulate matter and other air toxics. In 1995, Ontario Hydro’s five coal-fired stations accounted for between 10% and 18% of Ontario’s emissions of these four key pollutants. In a restructured market, owners will have profit motivations to increase utilization of these plants, possibly resulting in even higher emission levels.

At the same time, industry restructuring presents a unique opportunity to reduce the impact of this sector on the environment. This can be accomplished if Ontario’s new electricity system incorporates energy efficiency and greater utilization of low environmental impact generation systems, including cogeneration.

Also currently in progress is the National Climate Change Process. It is a multi-stakeholder consultation process aimed at providing guidance on the least-cost ways for Canada to meet its commitments for GHG reductions under the Kyoto Protocol. If Canada signs the Kyoto Protocol, it will be required to reduce its GHG emissions to 6% below their 1990 levels by the 2008-2012 time period. Several of the consultation tables of the Climate Change Process have identified cogeneration as a potentially cost-effective way to reduce GHG emissions.

The timing and purpose of this project, therefore, relate to the need to understand both the opportunities and challenges for cogeneration in the restructured Ontario electricity market and the opportunities for reducing GHG emissions through cogeneration.

1.1 Process for the Project

This project has two related elements: the estimation of economic cogeneration potential in Ontario, and the description of barriers which might prevent the realization of the potential. The first task is essentially analytical, requiring quantification of the total possible size of the market, the costs of cogeneration, and the costs of the alternatives. The second task is essentially a description of those factors which can present barriers.

For the analytical portion of the project, the methodology and data sources are described in later sections of this report. The economic potential is limited by two factors: the cost of the electricity and heat produced by cogeneration compared to its cost from alternative sources, and the existence of locations with a simultaneous demand for heat and electricity. The project used available data from various sources to assess the size of the total possible market. It used engineering cost data to analyze the cost of cogeneration. It used the best available forecasts for natural gas and electricity prices. These results were then combined to produce an estimate of the total economic potential.

For the barriers portion, the project combined the expertise of the project team with information obtained from industry participants. This information came from two Workshops with wide industry participation. The Workshops identified and verified the information on barriers. They also helped verify the technical data, especially cost data, from the analytical work.

1.2 Contents of the Report

The ultimate end of the report is to estimate the amount of economic potential for cogeneration in Ontario and to describe barriers which might prevent its realization. 

The next three sections of this report present the methodologies and results of the three steps in the analytical task of estimation of economic potential. The next section estimates the cost of cogeneration. Section 3 contains information on the total technical potential, and Section 4 estimates economic potential and the GHG implications of installing that much cogeneration.

Section 5 describes the barriers which may prevent the full economic cogeneration potential from being realized without some change in policy or the electricity market in Ontario.

Appendix A contains a report on the forecast used for the study of natural gas prices. Appendices B and C are reports from the first and second workshops.

2. Estimates of Cost of Cogeneration in Ontario 

Several different technologies and fuels can be used for cogeneration. The choice of technology is often related to the size of the application and to the nature of the steam host. Large-scale applications primarily use gas turbines. Smaller applications can use a variety of technologies. Costs in this study are estimated separately for these larger and smaller scale technologies.

Some industries, notably the forest products industries, generate waste materials which can be used as fuel. Some applications, like district heating, have widely dispersed customers for the heat output; others have single heat customers. These applications have differing cost characteristics.

The estimates of the cost of cogeneration in Ontario are built up from assumptions about the cost components: fuel, operating, and capital. Cost estimates were made separately for two size classes of cogeneration. AGRA Monenco, Inc estimated costs for the medium and large cogeneration applications (those above 10 MW of electricity generation capacity). Hagler Bailly estimated costs of smaller cogeneration facilities. 

Costs for each cogeneration technology are expressed as levelized unit energy costs (LUEC). LUEC is the present value of the cost of the electricity over the lifetime of the investment divided by the present value of the total of electricity produced over the lifetime. LUECs are used in this study because they allow direct cost comparisons between generation resources using different fuels and having different lifetimes and different time patterns of cash inflows and outflows.

In deciding on cogeneration installations, decision-makers do not typically refer to LUECs. The decision will be based on the projected energy costs for the total operation, including costs of fuels (gas, electricity, and other fuels), other energy operating costs, and capital costs. LUECs are used here because they allow comparison of costs across different technologies. 

However, since the actual decision is based on total cost for the installation, in many specific cases a cogeneration project is economic even though it uses a technology whose LUEC is above the market price of electricity. For example, if a steam host has a boiler that requires replacement, the incremental cost of the cogeneration can be reduced by the cost of the boiler, if the cogeneration facility can eliminate the need for it. Section 4 of this report discusses such cases in more detail.

Electricity generation cost estimates have three major components: capital cost, fuel cost, and operating and maintenance (O&M) costs. Capital costs reflect the fully installed cost for the technology. Fuel costs depend on fuel prices and conversion efficiency of the technology. O&M costs are sometimes estimated as a function of initial capital costs. Sources of data for these costs will be detailed with the assumptions below.

Costs are presented for three time periods: 2000, 2005, and 2010. All costs are presented in Canadian dollars, using a constant value for the year 2000. All costs are therefore in real terms. Forecast assumptions are also in real terms. Values are presented in real terms to avoid the need to inflate future costs and then discount by an interest rate adjusted for expected future inflation.

2.1 Assumptions

Table 2‑1
Forecast Gas Prices

[image: image1.wmf]5 yr 

5 yr 

5 yr 

YEAR

$

AAGR

$

AAGR

$

AAGR

2000

3.00

3.00

3.00

2005

2.51

-3.50%

3.15

1.00%

3.49

3.10%

2010

2.10

-3.50%

3.43

1.70%

4.07

3.10%

2015

2.34

2.20%

3.86

2.40%

4.65

2.70%

2020

2.61

2.20%

4.35

2.40%

5.31

2.70%

LOW CASE

BASE CASE

HIGH CASE



FORECAST GAS PRICES

Alberta Border

(All prices in $2000/Mcf)


2.1.1 Gas Prices

All the cost estimations used the same assumptions about the delivered price of natural gas, which fuels many of the potential applications. The forecast price of natural gas is the subject of a separate report, which is attached as Appendix A of this report. Forecasts are for delivered gas prices in three scenarios: a base case, with high and low cases.

Forecast gas prices are projected to 2020 for all three cases. Forecast prices were presented at the first Workshop. The gas prices used for this report are presented in Table 2‑1. 

2.1.2 Large and Medium Technologies

Capital costs for current installations rely on information from the AGRA Monenco generation cost model. These data represent current costs as obtained from previous confidential studies by AGRA Monenco and from recent manufacturer information. 

Fuel costs were determined by the heat rate and the cost of gas. Heat rates are from the same source as the capital costs, and for the base year, they represent the expected performance of currently available technologies. 

O&M costs are derived from a fixed and variable component. The fixed component represents such fixed expenses as insurance and local taxes, if any. The variable component represents the variable cost of operating the cogeneration facility.

Given these costs, the next step is to calculate the cost of power. To determine the cost of power produced by the large and medium cogeneration technologies, AGRA Monenco developed an income statement proforma financial model. This level of modeling was needed to allow analysis of the impacts of taxes on the cogeneration costs. The financial model was used to calculate the LUEC of each of the different plant capacities.

The assumptions used for the AGRA Monenco model were 

· Debt rate 
6%

· Debt term
20 years

· Debt/equity
75/25

· Hurdle rate (IRR)
13%

· Steam value ($/1000 lb) 
$7.51

· Capacity factor
93%

The debt rate represents a real interest rate for borrowing for projects of this kind. The IRR hurdle rate is a real rate that typical developers would require for a cogeneration project. 

The steam value is based on the commodity value of the gas displaced assuming 80% conversion efficiency for the gas, which is the value suggested by participants in the Workshops. For the early year cases, it is assumed that the cogeneration is being added to an existing facility. The steam is therefore given no credit for reductions in O&M or capital costs. 

2.1.3 Small Technologies 

Cost calculations for the smaller technologies were taken from the cost section of the PHB Hagler Bailly model DISGEN, which is used to calculate potential for (small-scale) distributed generation of all kinds including cogeneration. The DISGEN model bases decisions on total energy cost for the site. It therefore does not use LUECs directly; they were calculated for this project to allow comparison with the LUECs for the medium and large technologies.

These assumptions were consistent where possible with those for the larger technologies. Capital costs come from similar sources: previous confidential PHB Hagler Bailly projects, feedback from Workshop participants and other market sources in Ontario; information from manufacturers, and information from standard published industry cost sources. These sources also provide the information on the technical performance of the equipment, including heat rates and capacity factors. O&M costs were derived from the capital costs. For these cost estimates, all of the technologies are assumed to run at a 90% capacity factor. 

Gas costs were taken from the gas price forecast.

The LUECs were calculated assuming a 7-year payback period, spreading the capital costs equally over that period. This assumption reflects the small scale nature of these technologies and the likely approach of its owners.

The heat value was calculated by assuming that the heat requirement would otherwise be met by burning gas at 85% conversion efficiency. For this calculation, no credit is given for reductions in O&M or capital costs, because such savings are specific to particular applications. 

A key variable in evaluating these technologies is the ratio of electricity to thermal output. That ratio varies significantly between applications, depending on the nature of the heat demand and the technology. For this study, the electricity/thermal ratios vary from 0.5 to 4.0. All the fuel cell technologies have ratios above 1.2; among the other technologies, only the reciprocating engines have ratios that high. All the other thermal technologies have ratios well below one. These differences reflect the differences in the technologies. The fuel cells produce very little heat, giving much of their energy to electricity generation. The thermal technologies have much more waste heat available because they produce exhaust heat.

2.2 Cost Estimates

2.2.1 Large and Medium Technologies 

The current cost estimates for these technologies are based on actual costs or current planning costs of actual plants.

AGRA Monenco used its power project database to identify the cost of generating electricity and recovered thermal energy. The database is continuously updated with new supplier and market information. A number of sizes of cogeneration plants were selected based on actual configurations of cogeneration technologies
. The following candidate plants were analyzed: 

Combined cycle cogeneration: 
250, 150, 100 and 50 MW

Simple cycle cogeneration:

250, 40, 26 and 10 MW

Combined cycle cogeneration plants include a gas turbine, a steam turbine and a heat recovery steam generator (HRSG). A simple cycle cogeneration plant includes only a gas turbine and an HRSG. The significance of this difference is that a combined cycle plant typically transfers a greater proportion of the energy from input gas to electricity. In a simple cycle plant, a greater proportion of the energy of the input gas is applied to displacing thermal energy for space heating or industrial processes. 

For all of these plants, estimates were developed for total capital cost, variable operating costs, and fixed operating costs. Other operational cost estimates include expected plant life, plant availability, gas consumption, plant heat rate (without thermal sale), plant heat rate (with thermal sale) and steam output. All these parameters were quantified using AGRA Monenco’s cogeneration cost date base. 

The model was used to calculate levelized unit energy costs for six parameters including O&M, fuel cost, income tax, power price without thermal credit and power price with thermal credit (Table 2‑2.) All calculations are in real (constant dollar) terms.

The levelized unit energy cost of electricity ($/kWh) for each plant capacity was calculated as follows:

NPV of electricity revenue over 20 years

NPV of power output over 20 years (kWh)

Of all the cost components of gas fired cogeneration, the price of natural gas has the most significant impact on the levelized unit energy cost. The year one burner tip cost of gas ranges from $4.40/Mcf for large plants over 50 Mw to $6.73/Mcf for small units less than 500 kW. Long-term high, medium and low gas price forecasts developed by Hagler Bailly were applied to all gas fuelled plants. 

The 13% IRR hurdle rate represents the expectation of a typical developer, as estimated by AGRA Monenco.

Using Table 2‑2 for illustration, the following significant results are apparent. The capital cost per kW increases significantly as plant capacity decreases due to loss of economies of scale. Costs per kW range from a low of $774/kW for a 250 MW combined cycle plant to $2,039/kW for a 10 MW simple cycle plant. The results show the same relationship between plant size and the levelized cost of O&M. 

While levelized fuel cost increases as plant capacity decreases, the impact of the combined versus simple cycle plant configuration is also apparent. Using the 250 MW plants for purposes of illustration, the combined cycle plant has a lower fuel cost because a portion of the waste heat recovered is used to generate additional electricity through a steam turbine. 

Heat rates are a measure of the plant’s power generating efficiency. The total heat rates (without thermal credit) also show the influence of the steam turbine on reducing plant heat rates by increasing electricity output. The thermal credit heat rate incorporates the thermal sale into the plant’s overall efficiency. The formula for thermal credit heat rate is:

Total input energy (Btu)

Total electricity output (kWh) + Total thermal energy recovered (kWh)

For purposes of the study, the volume of thermal energy recovered was quantified differently in the case of the combined cycle and simple cycle plants. The volume of thermal energy recovered in the simple cycle plants was defined by that volume of waste heat rejected via the exhaust of the gas turbine that could normally be recovered for thermal sale using a state of the art HRSG. The results show that, with full heat recovery, simple cycle plants can achieve efficiencies of up to 80%. 

For combined cycle plants, the amount of electricity generation depends on the volume of steam diverted from the steam turbine to the heat application. For this analysis, the volume of steam diverted to use the thermal energy from the combined cycle plants was set at a level just sufficiently high to allow the plant to qualify for accelerated depreciation under the Class 43.1 efficiency provisions.

The levelized tax cost represents only corporate income tax paid after deduction of the class 43.1 accelerated capital cost allowance. Other taxes, including federal and provincial capital taxes, sales tax and municipal taxes are not included.

The levelized unit energy cost (LUEC) is shown both with and without the addition of thermal sales revenue (Thermal Credit). Again, the large proportion of thermal energy recovered for thermal sale in the case of the simple cycle plants is apparent. The Levelized Thermal Credit is substantially greater for the simple cycle plants than for the combined cycle plants.

It is important to note that the approach used in the study for quantifying thermal sale does not necessarily reflect the approach that would be taken in the field. In cases where power prices are relatively high, an investor may choose to minimize the use of waste heat for thermal sale. On the other hand, in cases where the site has a large heat demand, the investor might choose to divert a larger proportion of recovered heat to thermal sale. The limiting factor for heat recovery is the purchased energy load of the thermal host, proximate to the site of the generating plant.

Under the base case gas price assumptions, Table 2‑2 shows that, even with credit for the thermal sales, most of the cogeneration plants analyzed in this study will have LUECs above the 3.8¢/kWh revenue cap set for most of the output of Ontario Power Generation, Inc. under the Market Power Mitigation Agreement. Only the 250 MW simple cycle plant with maximum thermal sale achieves electricity prices low enough to compete with 3.8¢/kWh electricity. The implications of this result for future economic potential for cogeneration in Ontario will be analyzed in Section 4 of this report.

Resulting cost estimates are presented in Table 2‑2 for the base case gas prices. 

The cost estimates clearly show that there are economies of scale in cogeneration installations. The smaller installations have higher costs than the larger ones. This result is consistent with other studies. The degree of economies of scale in electricity generation have declined with the development of gas turbine technology. However, the larger cogeneration facilities considered here are about at the size that has been cited as the minimum size to achieve efficient scale.

The results also show that, for cogeneration applications, simple cycle gas turbines have lower costs than combined cycle turbines. This result is also not surprising. If the only output is electricity, combined cycle generators have lower costs because they can achieve higher overall conversion efficiencies by using the heat in the turbine’s exhaust gases to generate more electricity. A cogeneration application gets higher conversion efficiencies by direct use of the heat in the exhaust gases. The overall conversion efficiency for simple cycle turbines cogenerators is therefore typically higher than that of the CCGT, while the capital cost is usually lower because the steam turbine is not needed. This produces the result that simple cycle gas turbines are likely to be preferred for cogeneration applications, especially those with a high steam load relative to electricity load.

Table 2‑2
Large and Medium Cogeneration Technologies

[image: image2.wmf]Cost

($/MWh)

Type

Size

2000

2005

2010

(kW)

Microturbine

100

65.84

55.04

51.02

Solid Oxide-Atmospheric fuel cell

600

85.09

72.36

67.97

Solid Oxide-Press. Hybrid fuel cell

920

75.42

67.68

60.15

Reciprocating engines

300

77.43

74.18

69.34

Reciprocating engines

2500

59.81

57.01

52.58

Aeroderivative turbines

1500

73.81

66.50

59.37

Aeroderivative turbines

3000

63.00

56.03

49.34

Aeroderivative turbines

6000

58.22

49.49

46.41



Small

Cogeneration Technologies

LUEC Cost Forecast


2.2.2 Estimated Costs for Small Cogeneration 

Tables 2–3 and 2–4 show the derivation and results of the calculation of LUECs for smaller generation. Four technology types have been analyzed, with a selection of sizes for each type:

· Microturbines

· Fuel Cells

· Reciprocating Engines

· Aero Derivative Turbines.

Of these, two (reciprocating engines and aero derivative turbines) are established technologies with well-known cost and performance characteristics, while one type (microturbines) is being installed in some applications. The fourth type, fuel cells, has had fewer actual applications and is continuing to develop rapidly. The cost estimates for each type are subject to appropriate levels of uncertainty associated with their degree of development and actual application.

The cost and performance data for the cogeneration technologies are taken from the PHB Hagler Bailly DISGEN model, modified by inputs from Ontario industry participants. This model is used to estimate the potential for distributed electricity generation of all kinds. 

The cost data for DISGEN are regularly updated with information on actual installed cost of distributed generation facilities and on the current best engineering estimates of costs for generation technologies still in development. The assumptions for this analysis are intended to be compatible with that for the larger technologies. The 7-year payback period produces a rate of return similar to that of a 13% IRR. 

The 90% capacity factor assumed for these cost tables was chosen to show cogeneration favorably. It is assumed that an actual installation will be optimized for the sizes of the heat and electricity loads. Typically, heat loads are higher than electricity loads, so the electricity generation runs essentially to meet the electricity baseload plus as much of the heat load as that electricity generation will provide. Optimization considers the thermal/electricity ratios shown in Table 2‑3 and how well they match the energy and heat requirements for the specific installation.

Several results are apparent in Table 2‑4. First, as for the larger technologies, there are clear economies of scale. Within each technology, the larger the application, the lower the LUEC. These reflect the fixed costs of preparation of the installation as well as the lower cost per unit of capacity as the size of the application increases. 

Second, the Table shows that none of the small technologies would be competitive against electricity at a wholesale price of $0.038 per kWh, the price set under the Market Power Mitigation Agreement as a revenue cap for most of OPG’s generation. OPG will be required to pay rebates to all Ontario consumers should the average revenue for its generation capacity exceed this cap. Generation prices will be determined competitively and could be significantly above OPG’s revenue cap, although the revenue cap is expected to have an influence on prices.

[image: image3.wmf]Project Location

Market Segment

Electrical 

Capacity 

(MW)

Probability of 

Proceeding

Identified 10-40 MW

GTA

nug

10

H

N. Ont.

ind

20

M

Central Ont.

nug

20

M

GTA

inst

15

M

GTA

nug

20

M

GTA

ind

11

M

GTA

nug

25

M

Totals

10

121

Identified 40-100 MW

GTA

ind

40

M

East. Ont.

ind

40

M

East. Ont.

nug

50

M

GTA

nug

50

M

GTA

ind

40

M

East. Ont.

nug

90

L

NW Ont. Pulp & Paper 

nug

65

M

Totals

8

375

Identified 100-250 MW

Ottawa/Carlton Pulp & Paper

nug

153

L

East Ont.

ind

110

M

GTA

nug

150

M

GTA

nug

100

M

East. Ont. Pulp & Paper

nug

180

M

N. Ont.

nug

120

L

GTA

nug

100

L

GTA

nug

100

L

NW Ont. Pulp & Paper

nug

165

L

NW Ont.Pulp & Paper

nug

180

L

Totals

10

1,358

Identified 250 MW  and larger

GTA Pulp & paper

ind

250

H

Niag. Penn Pulp & Paper

ind

350

M

West. Ont.

nug

550

H

Niag. Penn.

nug

350

M

Totals

4

1,500

Total 

32

3,354

Plus 20% unidentified

688

Total potential

4,146

Table 2‑3
Indicative Performance Attributes of Small Cogeneration Systems

Table 2‑4
Indicative Cost Attributes of Small Cogeneration Systems

[image: image4.wmf]Indicative Cost Attributes of Small Cogeneration Systems

(Estimated Data for 2001) ($ figures in CD$ except where noted)

Installed

Capital 

O&M 

Fuel

Thermal

Adjusted

Size 

Technology

Fuel

Cost

Cost

Cost

Heat Rate

Availability

Taxes

LUEC

Credit

LUEC

(kW)

($/kW) (1)

($/MWh) (2)

($/MWh)

(Btu/kWh)

(%)

 ($/MWh)

 ($/MWh)(3)

 ($/MWh)

75

Microturbine

gas

1575

18.42

68.55

12,186

92%

115.51

37.64

77.87

100

Microturbine

gas

1350

15.04

63.97

11,373

92%

103.48

37.64

65.84

Fuel cells:

200

 Phosphoric Acid

gas

3000

17.64

47.98

8,530

98%

119.98

17.37

102.61

300

 Solid Oxide-Atmospheric

gas

3150

8.94

42.65

7,582

96%

108.67

15.05

93.61

600

 Solid Oxide-Atmospheric

gas

2850

5.84

41.72

7,417

95%

99.20

14.11

85.09

450

 Solid Oxide-Atmos. Hybrid

gas

2400

13.43

38.39

6,824

93%

95.30

11.29

84.01

900

 Solid Oxide-Atmos. Hybrid

gas

2250

13.43

38.39

6,824

93%

92.59

11.29

81.30

220

 Solid Oxide-Press. Hybrid

gas

2700

17.17

31.99

5,687

92%

98.08

5.65

92.44

920

 Solid Oxide-Press. Hybrid

gas

2250

8.31

31.99

5,687

92%

81.06

5.65

75.42

300

 Molten Carbonate

gas

3000

18.39

39.38

7,000

92%

112.12

11.29

100.83

1200

 Molten Carbonate

gas

2850

13.34

37.69

6,700

92%

102.67

11.29

91.38

250

 PEM

gas

3000

13.61

47.98

8,530

93%

115.95

18.82

97.13

300

Reciprocating engines

gas

1650

23.89

51.87

9,222

92%

105.66

28.23

77.43

1000

Reciprocating engines

gas

1463

14.86

45.70

8,124

92%

87.06

22.58

64.48

2500

Reciprocating engines

gas

1350

11.25

44.63

7,935

92%

80.34

20.53

59.81

5000

Reciprocating engines

diesel

900

20.08

66.75

7,417

95%

103.14

30.11

73.03

1500

Aeroderivative turbines

gas

2200

10.57

68.55

12,186

92%

118.98

45.16

73.81

3000

Aeroderivative turbines

gas

1900

8.05

58.16

10,339

92%

100.64

37.64

63.00

6000

Aeroderivative turbines

gas

1850

7.50

54.838

9,749

92%

95.854

37.64

58.22

(1) Including gas compression

Assumptions

    and moderate emission controls

Capacity Factor

90%

(2) With fixed O&M converted

Gas Price

5.625

$/MMBtu

Diesel Price

9

$/MMBtu

     at assumed capacity factor

5.33

$/GJ

8.53

$/GJ

(3) Most small cogen systems

Boiler Efficiency

85%

Capital Recovery

7

years

     limited to lower temperature

     applications -- exception small gas turbines

Exchange Rate Conversion

1.5

CD$/US$


All of the technologies except for the fuel cells are competitive against a delivered electricity price of $0.072 per kWh. That is the average delivered price expected to result from an average generation price of $0. 038. The pricing of transmission and distribution services is therefore important to the financial viability of the smaller cogeneration technologies. This impact will be discussed more fully in Section 4 of this report.

Table 2‑5 shows the forecast of cogeneration costs for some of the smaller size applications. The forecasts use the forecast of gas prices for this project along with forecasts of the capital costs and efficiencies of the smaller cogeneration technologies. The table shows the future costs falling. Costs fall because capital costs per kW decrease by 1-6% per year for these technologies. The more established technologies have the lower rates of capital price decrease. Efficiency is forecast to improve for all the technologies in the table, at rates from 0.2-1.1% per year. 

Table 2‑5
LUEC Cost Forecast for Small Cogeneration Technologies

[image: image5.wmf]Indicative Performance Attributes of Small Cogeneration Systems

(Estimated Data for 2001) ($ figures in CD$ except where noted)

Assumed

Total

Capacity

Electric-to

Output

Output

Conversion

Total

Total

Size 

Technology

Fuel

Factor

Heat Rate

Heat Rate

Thermal (E/T)

Electricity

Thermal

Efficiency

Heat 

Electricity

(kW)

(%)

(Btu/kWh)

(GJ/kWh)

Ratio

(GJ/h)

(GJ/h)

(%)

(Annual GJ)

(Annual GJ)

75

microturbine

gas

90%

12,186

0.013

0.6

0.27

0.45

75%

3,548

2,129

100

microturbine

gas

90%

11,373

0.012

0.6

0.36

0.60

80%

4,730

2,838

Fuel cells:

200

 Phosphoric Acid

gas

90%

8,530

0.009

1.3

0.72

0.55

71%

4,367

5,676

300

 Solid Oxide-Atmospheric

gas

90%

7,582

0.008

1.5

1.08

0.72

75%

5,676

8,515

600

 Solid Oxide-Atmospheric

gas

90%

7,417

0.008

1.6

2.16

1.35

75%

10,643

17,029

450

 Solid Oxide-Atmos. Hybrid

gas

90%

6,824

0.007

2.0

1.62

0.81

75%

6,386

12,772

900

 Solid Oxide-Atmos. Hybrid

gas

90%

6,824

0.007

2.0

3.24

1.62

75%

12,772

25,544

220

 Solid Oxide-Press. Hybrid

gas

90%

5,687

0.006

4.0

0.79

0.20

75%

1,561

6,244

920

 Solid Oxide-Press. Hybrid

gas

90%

5,687

0.006

4.0

3.31

0.83

75%

6,528

26,112

300

 Molten Carbonate

gas

90%

7,000

0.007

2.0

1.08

0.54

73%

4,257

8,515

1200

 Molten Carbonate

gas

90%

6,700

0.007

2.0

4.32

2.16

76%

17,029

34,059

250

 PEM

gas

90%

8,530

0.009

1.2

0.90

0.75

73%

5,913

7,096

300

Reciprocating engines

gas

90%

9,222

0.010

0.8

1.08

1.35

83%

10,643

8,515

1000

Reciprocating engines

gas

90%

8,124

0.009

1.0

3.60

3.60

84%

28,382

28,382

2500

Reciprocating engines

gas

90%

7,935

0.008

1.1

9.00

8.18

82%

64,505

70,956

5000

Reciprocating engines

diesel

90%

7,417

0.008

1.2

18.00

15.00

84%

118,260

141,912

1500

Aeroderivative turbines

gas

90%

12,186

0.013

0.5

5.40

10.80

84%

85,147

42,574

3000

Aeroderivative turbines

gas

90%

10,339

0.011

0.6

10.80

18.00

88%

141,912

85,147

6000

Aeroderivative turbines

gas

90%

9,749

0.010

0.6

21.60

36.00

93%

283,824

170,294


2.3 Electricity Prices

In the regulated electricity market, electricity prices were relatively easy to forecast. They were set to recover the full cost of the monopoly generator, Ontario Hydro. In a competitive electricity market, electricity prices are much more difficult to predict. Experience in other jurisdictions has shown that, after the introduction of competition, electricity prices become much more volatile.

PHB Hagler Bailly has recently completed a study for Ontario Power Generation (OPG) to determine the cost to the province of premature retirement of the coal-fired generation in the OPG fleet. As part of that study, PHB Hagler Bailly modelled the competitive electricity market for the years 2005-2012. The results of that model form the basis for a reasonable wholesale electricity price forecast for the Ontario market. 

The forecast in Table 2‑6 is based on the model results. For the first three years of the competitive market, the forecast assumes that the $38 per MWh revenue cap for OPG under the Market Power Mitigation Agreement (MPMA) effectively operates as both a cap and a floor. After the expiration of the revenue cap, the models indicate a small decrease in price. They then show electricity price in Ontario rising until the system requires new gas CCGT generation in 2012. From there, the market price remains that of the full cost of new CCGT generation, which is taken to be constant in real terms. Although the real price of gas is rising in the forecast, assumed continued improvements in the efficiency of generation offset the consequent cost increase.

[image: image6.wmf]Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Totals

Emissions from Cogeneration 

Large Applications

0.2

1.7

3.6

5.6

7.3

8.7

9.0

9.3

9.6

10.0

65.1

Small Applications

0.1

0.3

0.5

0.8

1.2

1.6

2.0

2.5

2.9

3.4

15.3

TOTAL EMISSIONS 

0.3

2.0

4.1

6.4

8.5

10.3

11.0

11.8

12.6

13.4

80.3

Avoided Emissions

Electricity Generation

0.8

5.1

10.6

16.5

21.8

24.3

25.9

27.6

29.3

31.2

193.1

Heat Production

0.2

0.8

1.6

2.5

3.3

4.7

5.3

5.8

5.5

6.0

35.6

TOTAL AVOIDED

1.0

5.9

12.2

19.0

25.1

29.0

31.2

33.4

34.8

37.2

228.8

NET EMISSION REDUCTION

0.6

3.9

8.1

12.6

16.7

18.7

20.2

21.6

22.2

23.8

148.4

Mtons CO2

GHG EMISSION SAVINGS FROM COGENERATION 

BASE CASE

Table 2‑6
Forecast of Electricity Prices in Ontario

3. Technical Potential for Cogeneration in Ontario 

The technical potential for cogeneration in Ontario is a function of the ability of the cogeneration technology to fulfill demands for simultaneous generation of heat and electricity, and of the number of applications which have demand matching the technology’s ability. Estimating the technical potential therefore requires information on both the demand and the technical ability.

The number of potential applications is finite for all the technologies. However, the larger the application, the smaller the number of potential sites. Where there are few potential sites, they can more readily be counted and the technical potential added up. Where there are very many sites, the economics of each cannot be analyzed in detail. For large applications, therefore, estimating technical potential is best done by counting potential sites. For smaller applications, an analytical or modelling technique is required to estimate the fraction of the total potential sites or of the total energy demand that can be met by cogeneration.

Most of the large-scale (above 50 MW) applications of cogeneration relate to industrial steam hosts. Only a few industries are large enough and need enough process steam or heat to create a possibility of applications on this scale. Examples include forest products, iron and steel making, chemicals, and refineries. For this scale of application, the counting method works well.

For medium scale applications, the steam hosts could be much more varied. They could include smaller firms with steam-intensive processes, or larger industries with less steam-intensive processes but large total needs. Examples include food processing or automobile and auto parts manufacturing. Some commercial enterprises can also support cogeneration installations of between 10 and 50 MW. Examples include hospitals, larger office buildings, and such other large institutions as universities. To estimate potential in these applications, a mix of counting methods and analytical techniques is used.

In the analysis, the large and medium size cogeneration applications are identified as industrial, while the smaller ones are identified as commercial. For both sizes, technical potential is estimated both with analytical techniques and by adding up potential sites. Analytical techniques are required for analysis of potential more than five years in the future, since the sites of future industrial or commercial developments are not known.

Methodology and Data Sources

3.1.1 Large and Medium Cogeneration 

Analytical Techniques 

The analytical technique uses aggregate data on energy use by industry. Such data are available for total commercial and industrial users in Ontario, including forecast data, from the NRCan publication Canada’s Energy Outlook, 1996-2020.
 That publication identifies total energy demand by sector for each province. 

Data have also been obtained from the Office of Energy Efficiency of NRCan. For the industrial sector, these data cover energy demand by fuel by industry group. 

The analytical techniques used for each sector are described in the next section.
Identified Sites 

Using identified sites is a counting method, gathering data on sites which have been identified as potentially developable. This method is expected to produce a lower estimate than an analytical technique would, since identified sites have been selected as those with greatest economic potential. This method is important to the analysis here, since it will provide information on how much cogeneration can be expected to be installed in Ontario in the near term.

The estimates for large and medium cogeneration sites are an update of the estimates made by AGRA Monenco for Ontario Hydro Services Company in the summer of 1999
. Those estimates were largely based on an inventory of potential sites for medium and large-scale cogeneration applications.

The estimates have been expanded using information on additional potential new cogeneration locations in Ontario. This information comes from inventories of potential cogeneration sites obtained from other stakeholders in the industry, including suppliers of equipment and fuel for potential new applications. The data also include new information on forest products industry operations, chiefly in northern Ontario. 

3.1.2 Small Cogeneration Applications

The estimate of technical potential for small and medium applications uses an analytic and modelling approach to the available data. For the PHB Hagler Bailly DISGEN model, the data base includes information on the number of buildings in the commercial sector by building type. In addition, NRCan’s Office of Energy Efficiency (OEE) has provided data on energy end use in the commercial sector. The data are broken out by nine building types and six end uses. These data allow an analysis of the total potential for simultaneous use of heat and electricity in the commercial sector. 

This analysis can indicate how much cogeneration could be supported if a given fraction of the total heat and electricity load in the province were met with cogeneration. These estimates then form the top of a range of possible cogeneration, or the total technical potential.

3.2 Estimates of Technical Cogeneration Potential

3.2.1 Estimates for Industrial Applications

Identified Sites

Table 3‑1 shows the estimates of the total technical potential for cogeneration applications in Ontario in the industrial sector, using the identified sites methodology. These estimates relate to large-scale applications as described above. 

The total technical potential for cogeneration in large and medium applications is shown as  4,146 MW.

[image: image7.wmf]MW

TWh.

2000

11214

28.43

2005

11966

31.06

2010

12676

33.09

2015

13371

34.96

2020

14037

36.44



POTENTIAL IN ONTARIO

Analytical Method

INDUSTRIAL COGENERATION

Table 3‑1
Industrial Cogeneration Potential in Ontario, February, 2000

The estimates above are from AGRA Monenco. The list of all cogeneration projects identified from data sources is updated from the list published in the AGRA Monenco report cited in the footnote above. The list used here identified three market segments: industrial, commercial, and institutional. If the project is to be sponsored by a non-utility generator, the segment is listed as NUG. In the table above, commercial and institutional projects have been removed to avoid double counting with the calculation of commercial potential in the next section of this report.

In the table, the probability of proceeding reflects the opinion of the data source at the time the project was identified. It does not necessarily refer to economic viability. The additional technical potential of 20% in unidentified projects is based on an estimate by AGRA Monenco. The project capacity refers to proposed size; the projects are not necessarily sized by embedded electrical or thermal loads
An approximate check is available on these estimates. The report “Opportunities for Increased Cogeneration in the Pulp and Paper Industry” was completed in March, 1999 by Neill and Gunther (Nova Scotia) Limited, for the Canadian Forest Service of NRCan.
 The report estimated total potential based on the existing and projected uses of energy in the pulp and paper industry. This estimate came from a technical analysis of the total energy used in the industry and its sources. The report estimated the potential as a total for all provinces using fossil fuel for electricity generation and pulp and paper operations. 

Assigning Ontario its share of the cogeneration potential equal to its share of total energy used nationally would probably underestimate total forest products cogeneration potential, since Ontario has a higher concentration on forest products than the average. Using this approximation, the estimate is for 906 MW of cogeneration potential in the Ontario pulp and paper industry. Table 3.1 identifies 1343 MW of pulp and paper projects, approximately 50% more than this estimate. Given the expectation that the 906 MW is an underestimate, this result is consistent with the Neill and Gunther study. 

Analytical Technique

The analytical technique used information from both the OEE data base and the NRCan Report. The OEE provided historical data on the total electricity demand by major industry group in Ontario. Totals from these data were compared to the industrial electricity demand shown in the 2020 Report, and they were compatible. The OEE data are available by industry. The analysis assumed all electricity demand in the pulp and paper, smelting and refining, petroleum refining, chemicals, iron and steel, and 25% in the “Other” category, could be met by cogeneration. 

Forecasts of future demand were obtained by applying the growth rate of industrial electricity demand from the NRCan Report to the base year load obtained from the OEE data.

In the industrial sector, the total energy supplied by natural gas is about twice that supplied by electricity. The maximum technical potential, therefore, would occur if the cogeneration is sized to meet the heat load, with the heat from the cogeneration displacing the natural gas. The cogenerators would then have excess electricity to sell in the market. For this analysis, it was assumed that half of the total gas used in the industries which can support cogeneration could be displaced by the heat product. This analysis produced a much higher estimate of the technical cogeneration potential than did an analysis assuming that the cogeneration would be sized to the electricity, not the heat, load.

Table 3‑2 shows the resulting potential estimates. These estimates are significantly higher than those obtained by counting up identified industrial sites. In 2000, the estimate from this analytical technique is over 11,000 MW of technical potential, as compared to under 5,000 MW from the AGRA Monenco data.

It should be noted that this estimate probably does represent an extreme value. If all the estimated technical potential were realized, industrial cogeneration would account for at least a third of the total electricity generation capacity in the province.

Table 3‑2
Industrial Cogeneration Potential in Ontario

[image: image8.wmf]Table 4.1

Cogeneration Potential in Ontario

Sensitivity Analysis based on 250MW Combined Cycle Cogeneration Case (CCC250 )

Parameter Changed

Changed

LUEC without

LUEC with

IRR

Thermal Credit 

[1]

Thermal Credit 

[2]

(Cdn$/MWh)

(Cdn$/MWh)

(%)

Base Case

46.72 Cdn$/MWh

50.82

46.72

13.00

Electricity Rate

38.00 Cdn$/MWh

-

-

N/A 

[3]

45.00 Cdn$/MWh

-

-

0.74

50.00 Cdn$/MWh

-

-

25.47

Heat Rate

-5%

49.13

45.03

13.00

-10%

47.44

43.34

13.00

Capital Cost

-5%

50.21

46.12

13.00

-10%

49.61

45.52

13.00

Note:

[1] 

LUEC is based on the cost of steam equal to zero Cdn$/klb

[2] 

LUEC is based on the cost of steam equal to 7.51 Cdn$/klb

[3] 

IRR in this case is not available since all the net cash flows along the study period are negative.


3.2.2 Technical Cogeneration Potential in Commercial and Institutional Applications

Table 3‑4 has an estimate of the technical potential for cogeneration for the commercial customer class in Ontario, which includes commercial and institutional customers. This estimate is an approximation.

The underlying data for this estimate come from the Office of Energy Efficiency (OEE) of NRCan. They provided historical data on energy end uses for nine building types for six end uses and six fuels. The data were for the years 1981-1997, inclusive. Table 3‑3 shows the data for 1997 for electricity and heat load for those building types which were analyzed for cogeneration potential. The table also shows the assumptions made for the analysis.

Table 3‑3
Data for Estimation of Technical Cogeneration Potential (Commercial Sector)

[image: image9.wmf]HIGH CASE (Low gas prices)

Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total

Large/Medium

90

458

639

679

869

452

304

156

161

173

3982

Small

65

72

78

85

100

133

132

137

158

177

1136

TOTAL 

155

529

717

763

969

585

436

293

319

350

5118

LOW CASE High gas prices)

Large/Medium

47

239

330

345

439

215

137

59

62

71

1944

Small

34

37

40

44

48

51

65

75

90

105

588

TOTAL

81

276

370

388

487

266

202

134

152

176

2532

Estimated Economic Cogeneration Installed Annually  

High and Low Cases

MW Installed in Year


The table shows the average annual growth rates over the entire historical period and the forecast average growth rates. For most building types, demand for both electricity and heat showed decelerating growth. The forecast continued that deceleration, making the forecast growth rate lower than the historical growth rate. For some building types, heating load had been falling; the forecast is for a continued, but slightly slower, decline.

For each building type, an assumption was made about the fraction of total electricity and energy use which occurred in larger buildings, capable of supporting the kind of cogeneration facility analyzed in the previous chapter. These estimates depend on that assumption which is shown in the last column of Table 3‑3. If the assumed fraction in large buildings rises, the estimated cogeneration potential will rise with it.

Data to support this assumption were available for two building types. An Ontario Hydro survey in the 1980s found that 46% of energy use in the office sector came in buildings with more than 200,000 square feet. The analysis assumed that such buildings would be candidates for cogeneration, so the fraction for office buildings is taken at 46%.

The Ontario Association of Physical Plant Administrators indicated that its 17 schools used a total of 12 PJ of energy. That is about 27% of the total energy estimated for the schools sector for 1998. The analysis assumed that such institutions have large buildings or groups of buildings which can host cogeneration applications (as several already do.) The fraction for schools buildings is taken at 27%.

Estimates for the amount of cogeneration which could be sustained in each of these building types are shown in Table 3‑4. 

In actual cogeneration applications, the technology will be chosen to meet the specific heat and electricity characteristics of the site. This analysis of technical potential requires some broad assumptions about technologies and relative heat and electricity demand. Where the energy requirement for heat is greater than that for electricity, a technology with a low electricity to thermal ratio is chosen. That could still produce electricity in excess of that required by the host. For this analysis of technical (not economic) potential, it is assumed that all such electricity could be sold into the grid. 

As Table 3‑3 shows, for four of the six building types analyzed, the total energy required for heat is significantly greater than that required for electricity. For these building types, the cogeneration potential is that amount of cogeneration which would be required to meet the total heat load in the large buildings.

In the other two building types, electricity demand is higher than heat demand. A cogeneration system which met the full electricity demand might produce much more heat than the buildings could use. For these types, a technology was selected with an appropriate size and electricity to heat ratio, and the technical potential estimate is for the electricity load. 

Table 3‑4 shows the technical potential in the commercial sector as roughly constant over time. While heat demand in some building types is forecast to grow, the growth is offset by declines in other building types.

[image: image10.wmf]Economic Potential at $50/MWh Electricity Price

Project Location

Market Segment

Electrical 

Capacity 

(MW)

Probability of 

Proceeding

Identified 100-250 MW

Ottawa/Carlton Pulp & Paper

nug

153

L

GTA

nug

150

M

East. Ont. Pulp & Paper

nug

180

M

NW Ont. Pulp & Paper

nug

165

L

NW Ont.Pulp & Paper

nug

180

L

Totals

5

828

Identified :250 MW  and larger

GTA Pulp & paper

ind

250

H

Niag. Penn Pulp & Paper

ind

350

M

West. Ont.

nug

550

H

Niag. Penn.

nug

350

M

Totals

4

1,500

Total economic potential

2,328

Table 3‑4
Commercial Sector Cogeneration Potential

3.2.3 District Heating

District heating is an application of cogeneration where the heat from the generator is used for space heating, water heating, and other uses in a group of buildings. The buildings need to be close to each other because the heat is distributed to them from the central source through pipes. District heating systems are economic when the buildings are dense enough to support the application.

The above analysis implicitly includes the technical potential for district heating in the commercial sector. The methodology starts with the total amount of energy used in heating and electricity generation, and estimates technical potential by building type according to estimates of building size. Since the technical potential estimate depends on the share of the building type that is large enough to consider cogeneration, the possibility of district heating is implicitly included. In effect, district heating is a specific way to implement the cogeneration which is calculated as being included in the technical potential.

3.2.4 Technical Cogeneration Potential in the Residential Sector

Cogeneration facilities in individual residences would be small, given the size of a typical household load. According to the OEE data, total non-electric energy used for space and water heating in the residential sector is about 2 ½ times as great as total electricity demand. The limiting factor in developing residential cogeneration facilities would therefore be electricity demand. This would be especially true for fuel cells, which as the table in Section 2 showed, have very high electricity/thermal output ratios (they have a low fraction of total energy available as heat.)

Current cogeneration technologies are not yet effective for the residential sector. It is difficult to make a quantitative estimate of the cogeneration potential when the technologies are still undergoing such rapid development.

3.3 Total Technical Potential

The total technical potential estimated for the industrial and commercial sectors is estimated to grow from about 14,000 MW in 2000 to over 16,000 MW by 2020. The total in 2000 is over half the expected annual peak load in that year. As already noted, these estimates represent extremes which are only possible if a very large fraction of the current natural gas use in the province, especially in the industrial sector, is replaced by cogeneration. 

Table 3‑5
Total Cogeneration Potential in Ontario

[image: image11.wmf]Fraction of

Electricity

Sector

Electricity

Heat

in Large

PJ

PJ

Electricity

Heat

Electricity

Heat

Buildings

Offices

46.34

52.44

4.35%

1.14%

2.60%

1.07%

46%

Health

9.78

41.79

0.28%

-2.50%

0.11%

-1.87%

40%

Schools

9.31

34.91

0.36%

-2.64%

0.37%

-2.00%

27%

Hotels

14.82

12.04

1.50%

0.65%

0.33%

0.43%

10%

Retail

55.05

33.16

1.74%

-0.89%

0.43%

-0.50%

10%

Other

20.26

35.29

1.99%

-1.35%

1.09%

-0.50%

5%

Data Source:  Office of Energy Efficiency, NRCan

Energy Use 1997

Growth Rate

Growth Rate

Data for Estimation of Technical Cogeneration Potential  

Commercial Sector

Ontario

Historical Data 

Assumptions

1981-97

2000-20

Average Annual

Average Annual


4. Economic Potential for Cogeneration in Ontario

The economic potential for cogeneration is the total amount of cogeneration which can make an economic return on its investment. That is defined as cogeneration which, after paying all of its costs, produces heat and electricity together more cheaply than they can be obtained from alternative sources. 

Economic potential is defined at a point in time. Realization of the potential takes place over time. When cost conditions first make a 250 MW cogeneration facility economic, it cannot be installed immediately. This study is intended to quantify the amount of cogeneration likely to be installed, given the assumed cost conditions and in the absence of barriers. The estimate uses different methodologies for large and small applications. 

4.1 Methodology 

Quantifying economic potential uses the cost and technical potential estimates of Sections 2 and 3 of this report. The analysis indicates which technologies have the potential to be economic, and what the total technical potential is. Then the economic potential is the application of economic technologies in locations where the technical potential exists. 

4.1.1 Large and Medium Scale

For large and medium scale generation, estimating economic potential at any time essentially amounts to an analysis of how many of the identified projects will be economic under the specific assumptions about their costs. The cost estimates of Section 2 showed that there are economies of scale for cogeneration projects. Therefore, larger projects may be economic when smaller ones are not. To determine which projects are economic, this methodology simply compares the avoided electricity cost to the LUEC of the technology which would be used. Thus, if the avoided electricity cost is above the LUEC of, say, a 100 MW project but below that of a 50 MW project, than all projects of at least 100 MW will be considered economic. This methodology assumes that most projects which could be economic in the short run have been identified. 

To translate this estimate of current economic potential into an estimate of the amount of cogeneration which would be likely to be installed in each year, the study has distributed the current potential over the following six years. It has followed a similar methodology to estimate the amount of economic potential identified in the future. To do this, economic potential is projected as a fraction of the total technical potential. The fraction is inferred from the fractions in the short run and the expected trend of cogeneration costs and electricity prices.

4.1.2 Small Scale Generation

To analyze the smaller projects, PHB Hagler Bailly used its DISGEN model. That model considers the total energy cost of candidate applications, and installs cogeneration when it is economic. The results from the application of the DISGEN model were not consistent with information from stakeholders and market participants on the actual amounts of cogeneration currently being installed in Ontario. Investigation of the causes for the discrepancy revealed several factors leading to cogeneration installation which the DISGEN model cannot consider. 

These factors are discussed in Section 4.2. That section also shows how the DISGEN model was adjusted to account for these factors. The forecast for cogeneration in the short term is derived from the market information combined with the DISGEN runs. The forecast for the longer term is inferred as a fraction of the estimated long-run potential.

4.2 Market Considerations

4.2.1 Electricity Prices

The price of electricity is a key variable in determining the economic potential. In the past, electricity prices could be predicted with some reasonable assurance. Electricity prices to consumers were set to recover the historical cost of the entire electricity supply system. Since most of those costs are known in advance, the price can also be known in advance with relatively little variance.

With the restructuring of the Ontario electricity market, however, forecasting prices has become more difficult. The wholesale price will be set by market forces. The wholesale electricity price forecast shown in Section 2.3 is the Hagler Bailly forecast derived from an earlier project. The wholesale market price is an annual average. This forecast does not address two important factors that determine the economic potential for cogeneration. The first of these factors is an input to the DISGEN model; the second cannot be.

The first factor is whether the electricity from the cogeneration facility is competing with the wholesale market price or the delivered price. The cost estimates of Chapter 2 showed that most cogeneration applications are not economic if they have to compete against a wholesale price at the level shown in Section 2.3. However, many of them are economic if they compete against the delivered retail price of electricity, since the delivered retail price is likely to be about twice the wholesale price.

The difference between the wholesale price and the delivered price will have several components: transmission charges, distribution charges, the IMO uplift, and a competition transition charge. In turn, each of these charges can have several components. The question of whether self-generation installations pay these charges has only been partly settled. The Ontario Energy Board (OEB) has ruled that distributors containing new self-generators do not have to pay the network portion of Hydro One’s transmission tariff on the new self-generation capacity. Distributors containing self-generators below 1 MW capacity will not have to pay any transmission tariff on that capacity
.

The IMO Technical Panel is currently discussing the rules which implement this decision, as well as the question of whether self-generators are responsible for all or some of the IMO’s charges. The issue of billing of new self-generators is therefore not yet fully resolved. However, the wording of the OEB’s decision indicated that it favored the establishment of new generation in the province.

For this report, the cogeneration potential estimates will consider two extremes of the resolution of the pricing issue: potential if the cogeneration must compete with the wholesale electricity price, and potential if the cogeneration competes with the delivered retail price. The DISGEN model explicitly includes prices against which the cogeneration competes, as well as prices it gets for outside sales. The delivered vs. wholesale price factor can therefore be considered directly in the model.

The second factor is price volatility. Because electricity will be sold on an hourly market, there is likely to be more attention to the hourly changes in market-clearing prices. Periods of shortage can create “price spikes,” when the price rises to well above (an order of magnitude or more) its average level. If the Ontario market does move to Locational Marginal Pricing, the spikes are likely to be more pronounced in some local areas. 

Potential generation entrants will expect to take advantage of the price volatility. If their systems are flexible enough, they can operate only during those hours when the spot electricity wholesale price is above their cost of production. Even though their costs are above the average price, such generators can earn economic returns by keeping their average received price above their average total costs.
 This strategy is more difficult to follow for many potential cogeneration operators than for operators of merchant combined cycle or simple combustion turbine plants. Cogenerators must able to meet the steam or heat loads of their thermal hosts, which could preclude shutting down when prices are low. 

Load following capability is a factor cited by cogeneration owners as making some new investments economic. It is applicable in installations where a backup steam or heat system is available for use when the cogeneration facility is shut down. The effect of this factor on cogeneration potential is difficult to consider in the DISGEN model because it is so specific to individual sites and agreements between thermal hosts and electricity providers. For the runs for this project, this factor was approximated by increasing the penetration rate of cogeneration when it had a small cost advantage or disadvantage.

4.2.2 Capital Costs

Capital costs for large, medium and small cogeneration applications were quantified in Section 2 of this report. These costs are for new cogeneration applications using the best available equipment for each of the applications listed.

Stakeholders indicated that the actual capital costs for specific applications might be lower than those indicated. For example, where a facility has a boiler that has reached the end of its life, the cost of the cogeneration is only the incremental cost of adding electricity generation to the boiler cost. For a new installation which needs both steam and electricity, the cost of cogeneration is again only the incremental cost of the cogeneration over the cost of the boiler that would be needed anyway.

Since these effects are so specific to particular applications, they cannot be taken into account either in the large applications cases or in the DISGEN model. They have been considered in the revised DISGEN model runs by reducing capital costs by an arbitrary amount. 

4.2.3 Fuel Costs

Fuel costs were discussed in Section 2. Stakeholders did not indicate that specific potential cogeneration applications would have any fuel cost advantage that was not considered in the analysis or the DISGEN model. 

4.2.4 Other Factors

Other considerations may lead owners or developers to install cogeneration in sites where the economics are only marginally positive or even marginally negative.

In some uses, cogeneration is a more reliable electricity source than power from the local distribution company. Most power outages are caused by the distribution system. The next most likely source of an outage is the transmission system. Many customers with a need for highly reliable electricity supply install self generation. When such customers also have a suitable heat load, they might install cogeneration instead of backup generation. This factor can lower the effective capital costs for cogeneration, because the capital cost would be only the differential between the cost of the cogeneration and the cost of the simple backup. 

Cogeneration also increases reliability, because it provides a source of power that is available even when the transmission or distribution system fails. For some companies, the value of the increased reliability may make cogeneration economic even if its monetary cost is higher than that of central supply. 

For the runs in the DISGEN model, these factors are represented by both the reduction in capital costs and in the increased penetration of marginally economic or marginally uneconomic cogeneration.

Another factor which could lead to installation of cogeneration which is not economic in the market sense is the fact that cogeneration generally makes more efficient use of the primary energy supply than do non-cogeneration applications. It can therefore be seen as less environmentally harmful. Some users may prefer lower impact modes of electricity generation. This factor is considered in the model by adjusting the penetration rate of marginally economic or marginally uneconomic cogeneration.

4.2.5 Sensitivity Analysis

Several factors crucial to the economics of cogeneration have been identified in this study. These include the price of natural gas, the capital cost of the equipment, and the price of the displaced electricity. The cost sensitivities for some of these factors are shown in Table 4-1. The analysis will show the sensitivity results for the high and low natural gas prices.

The economic potential for large and medium scale cogeneration was assessed by undertaking sensitivity analysis on those variables which can impact the economic viability of cogeneration and which are most likely to move in a direction that improves the economic viability. The parameters tested include market electricity sales rates of $38, $45 and $50 per MWh, heat rate improvements of 5 and 10% and capital cost re installed kW reductions of 5 and 10%. The results of the analysis are shown on Table 4.1.

Table 4‑1
Sensitivity Analysis of Cogeneration Costs

[image: image12.wmf]Cogeneration Potential in Ontario

Estimated Total Costs of Electricity Generated

Base Case Gas Prices

Type of Unit

Rated Output

Fuel

Capital Cost

[1]

Levelized 

Levelized

Plant

Thermal Credit

Availability

Levelized

LUEC without

Levelized 

LUEC with

O&M Cost

Fuel Cost

Heat Rate

[2]

Heat Rate

Tax

[3]

Thermal Credit 

[4]

Thermal Credit

Thermal Credit 

[5]

(MW)

(Cdn$/kW)

(Cdn$/MWh)

(Cdn$/MWh)

(Btu/kWh)

(Btu/kWh)

(Cdn$/MWh)

(Cdn$/MWh)

(Cdn$/MWh)

(Cdn$/MWh)

Cogeneration

[6]

Gas Turbine Plants

CCC 250

Gas

774

4.96

34.73

6,705

< 6,000

93.0%

1.27

50.82

4.21

46.72

SCC 250

Gas

814

4.97

54.41

10,506

4,330

93.0%

1.52

70.62

32.69

38.80

CCC 150

Gas

813

6.25

39.95

7,715

< 6,000

93.0%

1.36

57.80

9.33

48.71

CCC 100

Gas

1,131

9.36

38.94

7,519

< 6,000

93.0%

2.10

64.88

8.65

56.46

CCC 50

Gas

1,626

18.61

37.61

7,262

< 6,000

93.0%

3.25

80.55

6.98

73.76

SCC 40

Gas

1,290

17.29

44.81

8,652

4,350

93.0%

2.65

81.00

24.78

56.88

SCC 26

Gas

1,563

20.37

56.01

10,815

4,840

93.0%

3.29

99.23

36.40

63.80

SCC 10

Gas

1,600

22.50

62.50

11,124

4,780

93.0%

4.37

116.05

39.35

78.50

Note:

[1]

 Excludes Interest during Construction 

[2] 

Include 3% Degradation.

[3] 

Tax cost includes Income Tax only. Capital taxes, GST and municipal taxes are not included.

[4] 

LUEC is based on the sales value of steam equal to zero Cdn$/klb

[5] 

LUEC is based on the sale value of steam equal to 7.51 Cdn$/klb

[6] 

Thermal recovery of CCC plants is designed to just meet the Class 43 heat rate of 6000 Btu/kWh.

Legend:

CCC250 - 250MW Combined Cycle Cogeneration*

SCC250 - 250MW Simple Cycle Cogeneration*

CCC150 - 150MW Combined Cycle Cogeneration*

SCC40   - 40MW Simple Cycle Cogeneration*

CCC100 - 100MW Combined Cycle Cogeneration*

SCC26   - 26MW Simple Cycle Cogeneration*

CCC50   - 50 MW Combined Cycle Cogeneration*

SCC10   - 10MW Simple Cycle Cogeneration*

* Class 43.1 eligible

[image: image13.wmf]5 yr 

5 yr 

5 yr 

YEAR

$

AAGR

$

AAGR

$

AAGR

2000

3.00

3.00

3.00

2001

2.90

3.03

3.09

2002

2.79

3.06

3.19

2003

2.70

3.09

3.29

2004

2.60

3.12

3.39

2005

2.51

-3.50%

3.15

1.00%

3.49

3.10%

2006

2.42

3.21

3.60

2007

2.34

3.26

3.71

2008

2.26

3.32

3.83

2009

2.18

3.37

3.95

2010

2.10

-3.50%

3.43

1.70%

4.07

3.10%

2011

2.15

3.51

4.18

2012

2.19

3.60

4.29

2013

2.24

3.68

4.41

2014

2.29

3.77

4.53

2015

2.34

2.20%

3.86

2.40%

4.65

2.70%

2016

2.39

3.95

4.78

2017

2.45

4.05

4.91

2018

2.50

4.15

5.04

2019

2.56

4.25

5.17

2020

2.61

2.20%

4.35

2.40%

5.31

2.70%

BASE CASE

HIGH CASE

LOW CASE

Alberta Border

FORECAST GAS PRICES

(All prices in $2000/Mcf)


The economic potential for cogeneration in Ontario will be estimated in this study for three cases, a base case and high and low scenarios. Much of the differential between these will be based on the difference between assumptions. 

4.3 Cogeneration Potential: Base Case

4.3.1 Economic Potential for Large and Medium Scale

Table 4.2 shows which cogeneration technologies are economic under the base electricity price case. The electricity price of $50 per MWh is about the expected market price of $38 per MWh plus the credit for the network transmission charge. 

[image: image14.wmf]Transmission

YEAR

Tolls 

Sudbury

Toronto

Sudbury

Toronto

Sudbury

Toronto

2000

0.98

0.40

0.40

0.80

0.80

2.50

2.75

2001

0.97

0.40

0.40

0.80

0.80

2.44

2.69

2002

0.95

0.40

0.40

0.80

0.80

2.39

2.63

2003

0.94

0.40

0.40

0.80

0.80

2.34

2.57

2004

0.93

0.40

0.40

0.80

0.80

2.29

2.52

2005

0.91

0.40

0.40

0.80

0.80

2.24

2.46

2006

0.90

0.40

0.40

0.80

0.80

2.19

2.41

2007

0.89

0.40

0.40

0.80

0.80

2.14

2.35

2008

0.87

0.40

0.40

0.80

0.80

2.09

2.30

2009

0.86

0.40

0.40

0.80

0.80

2.05

2.25

2010

0.85

0.40

0.40

0.80

0.80

2.00

2.20

2011

0.84

0.40

0.40

0.80

0.80

1.97

2.17

2012

0.83

0.40

0.40

0.80

0.80

1.94

2.13

2013

0.82

0.40

0.40

0.80

0.80

1.91

2.10

2014

0.82

0.40

0.40

0.80

0.80

1.88

2.07

2015

0.81

0.40

0.40

0.80

0.80

1.85

2.04

2016

0.80

0.40

0.40

0.80

0.80

1.83

2.01

2017

0.79

0.40

0.40

0.80

0.80

1.80

1.98

2018

0.78

0.40

0.40

0.80

0.80

1.77

1.95

2019

0.78

0.40

0.40

0.80

0.80

1.75

1.92

2020

0.77

0.40

0.40

0.80

0.80

1.72

1.89

Distribution Tariffs for Cogeneration

DISTRIBUTION AND TRANSMISSION CHARGES

(All prices in $2000/Mcf)

>50 MW

10 MW

<500 kW

Table 4‑2
Return to Cogeneration: Large and Medium Scale

[image: image15.wmf]Sudbury

Toronto

YEAR

Low

Base

High

Low

Base

High

Low

Base

High

Low

Base

High

2000

4.38

4.38

4.38

4.78

4.78

4.78

6.48

6.48

6.48

6.73

6.73

6.73

2001

4.26

4.40

4.46

4.66

4.80

4.86

6.31

6.44

6.50

6.55

6.69

6.75

2002

4.15

4.41

4.54

4.55

4.81

4.94

6.14

6.40

6.53

6.38

6.64

6.77

2003

4.03

4.43

4.63

4.43

4.83

5.03

5.97

6.37

6.56

6.21

6.60

6.80

2004

3.93

4.45

4.72

4.33

4.85

5.12

5.81

6.33

6.60

6.04

6.56

6.83

2005

3.82

4.47

4.81

4.22

4.87

5.21

5.66

6.30

6.64

5.88

6.53

6.87

2006

3.72

4.51

4.90

4.12

4.91

5.30

5.51

6.29

6.69

5.73

6.51

6.91

2007

3.62

4.55

5.00

4.02

4.95

5.40

5.36

6.29

6.74

5.58

6.50

6.95

2008

3.53

4.59

5.10

3.93

4.99

5.50

5.22

6.28

6.80

5.43

6.49

7.00

2009

3.44

4.64

5.21

3.84

5.04

5.61

5.08

6.28

6.86

5.29

6.48

7.06

2010

3.35

4.68

5.32

3.75

5.08

5.72

4.95

6.28

6.92

5.15

6.48

7.12

2011

3.39

4.75

5.42

3.79

5.15

5.82

4.96

6.32

6.99

5.16

6.52

7.19

2012

3.43

4.83

5.53

3.83

5.23

5.93

4.97

6.37

7.07

5.16

6.56

7.26

2013

3.47

4.91

5.63

3.87

5.31

6.03

4.98

6.42

7.15

5.17

6.61

7.34

2014

3.51

4.99

5.75

3.91

5.39

6.15

4.99

6.47

7.23

5.18

6.66

7.42

2015

3.55

5.07

5.86

3.95

5.47

6.26

5.01

6.52

7.31

5.19

6.71

7.50

2016

3.59

5.16

5.98

3.99

5.56

6.38

5.02

6.58

7.40

5.20

6.76

7.59

2017

3.64

5.24

6.10

4.04

5.64

6.50

5.04

6.64

7.50

5.22

6.82

7.68

2018

3.68

5.33

6.22

4.08

5.73

6.62

5.06

6.70

7.59

5.23

6.88

7.77

2019

3.73

5.42

6.35

4.13

5.82

6.75

5.08

6.77

7.70

5.25

6.94

7.87

2020

3.78

5.52

6.48

4.18

5.92

6.88

5.10

6.84

7.80

5.27

7.01

7.97

10 MW

<500 kW

DELIVERED PRICES FOR GAS FOR COGENERATION

(All prices in $2000/Mcf)

LOW, BASE AND HIGH CASES

>50 MW


Only large-scale cogeneration would be economic under this price regime. Table 4-3 below shows all those projects from the list in Table 3-1 which are above 150 MW and would therefore be economic competing with an average electricity price of $50 per MWh. 

[image: image16.wmf]Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total

Potential

50

55

60

65

72

88

119

122

123

125

879

Estimated Economic Cogeneration Installed Annually  

Small Scale Applications

Base Case

MW Installed in Year


Table 4‑3
Estimated Economic Potential: Large/Medium Scale

Table 4-3 shows the amount of large and medium scale cogeneration estimated to be economic at this time. To estimate how much cogeneration will be installed over time, this study uses an S-curve for the penetration of the potential. It spreads the installation of this potential out over six years, with the peak coming in the third and fourth years. This timing accounts for both decision and construction periods.

In addition, the amount of economic cogeneration will increase over time as both the technology becomes cheaper and as the Ontario industrial sector expands. Table 3-5 showed an estimate of the total technical potential for the next 20 years. Using that estimate, the current economic potential is about 23% of technical potential. In the base case, the fraction of total technical potential that is economic was assumed to increase by about 0.5% per year to 2008, and by 1% per year from then to 2010. The proportion of economic cogeneration is expected to increase due to lower costs of cogeneration and increasing electricity prices.

The estimate of future installations applied the same S-curve to the amount of increased economic potential created in each year. Economic potential grows because technical potential grows and the proportion that is economic increases, under the assumptions used here.

As with the results for small scale cogeneration, the totals in Table 4-3 do not include several announced or prospective projects in the 40-60 MW range which appear likely to proceed. Some of the same considerations leading to an underestimate for the small scale cogeneration projects likely apply in this case. Therefore, in deriving the annual installation rates, the current amount of economic potential was increased by 5% over the amount shown in Table 4-3. 

The resulting estimates of installed large and medium scale cogeneration are shown in Table 4-4.

Table 4‑4
Economic Cogeneration Installed: Large and Medium Scale

[image: image17.wmf]Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total 

Potential

73

493

634

657

558

210

89

90

94

104

3002

MW Installed in Year

Estimated Economic Cogeneration Installed Annually  

Large and Medium Scale Applications

Base Case


Economic Potential for Small Scale Cogeneration

The potential for small-scale cogeneration was estimated with the DISGEN model. In the first years, the DISGEN model produces low totals. These totals disagree with the strong feedback received from industry participants in Ontario. The reasons for this discrepancy were analyzed in Section 4.2 of this report. 

Several basic parameters in the DISGEN model were altered in an attempt to produce results that reflected this feedback. The most important changes were a reduction in the price of capital and an increase in the market penetration rates. These changes produced higher installation rates, but were in the early years still below the levels indicated by the industry feedback.

The results shown in Table 4-5 below, therefore, represent a blend of two sources: in the first years, they reflect the information received from industry participants; in the later years, they are the results from the DISGEN model runs with the base case assumptions. 

Table 4‑5
Economic Cogeneration Installed: Small (0.25-10 MW)

[image: image18.wmf]Price

Year

($/MWh)

2001

38

2005

37

2010

43

2015

47

2020

47

Forecast of

Electricity Prices in

Ontario

Annual Averages


4.3.2 Total Economic Cogeneration Installed Annually: Base Case

The total cogeneration installed annually is the sum of the large and small scale applications. It is shown below in Table 4-6.

Table 4‑6
Total Economic Cogeneration Installed Annually: Base Case

[image: image19.wmf]Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total

Potential

50

55

60

65

72

88

119

122

123

125

879

Estimated Economic Cogeneration Installed Annually  

Small Scale Applications

Base Case

MW Installed in Year


4.4 Cogeneration Potential: Alternate Cases

The amount of economic cogeneration is determined by many variable factors, most of which have been discussed in this report. The estimates of installed cogeneration given above are derived from a single set of assumptions about the values of these variables. Given the uncertainty about these factors, it is useful to provide some information on the results under different assumptions.

Estimates of the amount of cogeneration installed per year were made for the two alternative gas price cases. The prices for the alternative cases are shown in Table 2-1 and a more detailed explanation is provided in Appendix A. 

To estimate the amount of large and medium scale cogeneration which would be installed, the same methodology was used as for the base case. AGRA Monenco provided estimates of the LUECs of the available technologies. With the information on currently identified projects, this produced an estimate of the amount of such cogeneration which would be economic now. This estimated amount was then installed over a six-year period, using an S-curve for installation. 

Changes in the gas price will not change the amount of technical cogeneration potential, so the high and low cases assumed that the initial fraction of total potential grew faster or slower than it did in the base case. For the high gas price case, the fraction of the technical potential that is economic grows by 0.4% per year until 2008, and at 0.75% per year after that. For the low gas price case, the fraction grows by 1% per year until 2008, and 1.5% per year after that.

Table 4-7 shows the results for the high and low cases. 

[image: image20.wmf]Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total 

Potential

73

493

634

657

558

210

89

90

94

104

3002

MW Installed in Year

Estimated Economic Cogeneration Installed Annually  

Large and Medium Scale Applications

Base Case

Table 4‑7
Estimated Economic Cogeneration Installed Annually: High and Low Cases

The study also explored sensitivity to transmission pricing for new cogeneration. Under the Hydro One tariff as approved by the Ontario Energy Board, embedded generators will not pay network transmission charges. Since many of the cogeneration applications are likely to be embedded in a distribution company’s territory, while others are not, the sensitivity of the amount of cogeneration installed, relative to the transmission charges, was explored.

The exploration was done with the DISGEN model, which only considered small scale cogeneration applications. According to the DISGEN model, removing transmission charges from applications of between 1 and 10 MW would roughly double the amount of small scale cogeneration which would be installed over the period up to 2010.

4.5 GHG Reductions Associated with Cogeneration 

GHG reductions associated with cogeneration depend on the emissions rates of the cogeneration facilities and the emissions rates of the facilities they displace. 

Emissions rates for the cogeneration facilities can be inferred from their heat rates. The heat rates give the number of Btus per kWh for the cogeneration. Assuming that all the input heat energy comes from natural gas, emissions rates are readily available to convert the energy content of the natural gas into CO2 emissions.

The heat rates for the large and medium technologies are close to each other. To estimate the GHG emissions, a weighted average of the heat rates was constructed.

For the small technologies, the heat rates can vary significantly across technologies. Heat rates were derived as a weighted average of the heat rates of the technologies. The weights assumed that most of the electricity would be provided by gas turbines, with some contribution from both gas and diesel reciprocating engines. Fuel cell contributions were assumed to increase over time.

Cogeneration displaces electricity generation and steam or other heat generation. 

To estimate GHG emissions from electricity generation requires knowing what the fuel source would have been. For this study, an assumption is made that the displaced fuel source would be coal. Emission rates for coal-fired plants in Ontario are available from a report by Acres Management Consulting for Ontario Power Generation, Inc.
 The Acres report indicates that the emissions rates vary by plant, with over 10% difference between the highest and the lowest. However, the plants most likely to be displaced by cogeneration in southern Ontario (Nanticoke, Lambton, and Lakeview) have very similar CO2 emission rates. This estimation used a weighted average of the existing OPG coal-fired station emission rates.

Cogeneration also avoids the use of natural gas or other fuels to generate heat or steam. For this estimate, it was assumed that the avoided fuel would be natural gas. The natural gas would have been used to generate steam at the average efficiency rate of the boilers, which is assumed at 80%. Avoided GHG emissions from the steam generation are therefore computed assuming that the equivalent amount of end-use heat would have been produced by steam boilers operating at 80% efficiency.

The emissions from each type of cogeneration are readily available from the heat rates for the equipment. The heat rates translate directly to quantities of natural gas consumed. 

Table 4‑8 below shows the GHG emissions of the cogeneration and the emissions avoided by the use of cogeneration. Cogeneration using gas produces only about 1/3 the emissions for equivalent electricity and heat use from coal-fired and natural gas sources.

Table 4‑8
Net Reduction in GHG Emissions from Cogeneration 

[image: image21.wmf]Project Location

Market Segment

Electrical 

Capacity 

(MW)

Probability of 

Proceeding

Identified 10-40 MW

GTA

nug

10

H

N. Ont.

ind

20

M

Central Ont.

nug

20

M

GTA

inst

15

M

GTA

nug

20

M

GTA

ind

11

M

GTA

nug

25

M

Totals

10

121

Identified 40-100 MW

GTA

ind

40

M

East. Ont.

ind

40

M

East. Ont.

nug

50

M

GTA

nug

50

M

GTA

ind

40

M

East. Ont.

nug

90

L

NW Ont. Pulp & Paper 

nug

65

M

Totals

8

375

Identified 100-250 MW

Ottawa/Carlton Pulp & Paper

nug

153

L

East Ont.

ind

110

M

GTA

nug

150

M

GTA

nug

100

M

East. Ont. Pulp & Paper

nug

180

M

N. Ont.

nug

120

L

GTA

nug

100

L

GTA

nug

100

L

NW Ont. Pulp & Paper

nug

165

L

NW Ont.Pulp & Paper

nug

180

L

Totals

10

1,358

Identified 250 MW  and larger

GTA Pulp & paper

ind

250

H

Niag. Penn Pulp & Paper

ind

350

M

West. Ont.

nug

550

H

Niag. Penn.

nug

350

M

Totals

4

1,500

Total 

32

3,354

Plus 20% unidentified

688

Total potential

4,146


5. Analysis of Barriers to Cogeneration

At this time, there remains a great deal of uncertainty regarding the regulatory treatment of cogeneration facilities. This uncertainty includes questions surrounding the regulatory treatment of transmission and distribution tariffs for cogeneration and environmental approvals requirements. Stakeholders noted that major investments are unlikely to be made until the content of these regulations becomes clear.

This uncertainty is a short-term concern that will be rectified in the near future as the required regulations are developed and introduced. Some of these uncertainties have already been reduced by regulatory decisions or government policy measures.

This section of the report analyses some of the barriers to the installation of economic cogeneration projects. In this context, barriers are defined as factors that could prevent or slow the use of cogeneration in applications where it is otherwise economic. This analysis is based on the barriers that were identified and discussed at this project’s two Stakeholders Workshops, a review of previous studies on such barriers, and the study team’s understanding of these barriers. 

The description and characterization of the barriers in this section is primarily from the point of view of the stakeholders, as expressed in the Workshops. Reports from the Workshops are attached as Appendices B and C.

In order to be most useful, the focus of this analysis of barriers is on those for which potentially viable solutions can be identified. Those barriers for which such solutions could not be identified are discussed separately.

This analysis consists of a description of the barriers, how they impact the potential for cogeneration and the identification of possible solutions. The identified barriers have been classified into three categories: market barriers, institutional barriers and regulatory barriers. Where appropriate and possible, closely related barriers have been analyzed together. 

The scope of this project does not include an assessment of the cost/benefits of these possible solutions or their potential impact on the future utilization of cogeneration. 

Market Barriers

5.1.1 Low Price for Electricity

A low price for electricity is likely the most significant of the many barriers analyzed in this chapter. Some stakeholders characterized prices as artificially low.

Several factors have been identified that have resulted, in the view of stakeholders, in artificially low prices for electricity, particularly nuclear-generated electricity, and will continue to do so unless rectified. Heavy public capital contributions, including the writedown of the stranded debt, are seen as having allowed this highly capital-intensive form of electricity generation to become competitive. Other factors include the concern by many that the full costs associated with the decommissioning of nuclear plants at the end of their useful life and the long-term costs to store spent nuclear fuel are currently not included in the costs of nuclear power. The billions of dollars that were invested by the government over the past forty years in the research and development of CANDU reactors are also not included in the current cost of nuclear power in Ontario. 

Another important factor that, in the view of stakeholders, has led to artificially low prices for electricity in Ontario is the failure of the current pricing system to include the full environmental costs associated with generating electricity from coal and oil-fired plants. These externalities include, but are not limited to, the cost of the impact on human health and the environment of emissions such as SO2, NOX, CO2, mercury and other toxics.

The decision of the Ontario government to freeze electricity rates in 1994 has also produced what some stakeholders see as artificially low electricity prices in Ontario. Average electricity rates were frozen due to concerns that, without such measures, high rates could jeopardize the competitiveness of Ontario’s industrial and commercial sectors. The last electricity price increase in the province was seven years ago. The move to a competitive electricity supply market can be expected to remove any “price freeze” barrier.

The range of government actions suggested by stakeholders which can address this barrier include the following:

· Full or at least partial exemption from the Debt Retirement Charge (DRC) for newer, cleaner means of electricity generation, such as cogeneration.

· Ensure that OPG or any subsequent owner of Ontario’s nuclear assets allocates sufficient funds for the decommissioning of nuclear plants at the end of their useful and the long-term costs to store spent nuclear fuel.

· Environmental policies which impose costs for atmospheric emissions, especially of NO and SO2.

5.1.2 Artificially Low Cost to Reactivate 5 GW Nuclear Capacity

The Pickering and Bruce Nuclear stations have a total of about 5 GW of potential generation capacity that is not in service. Although the cost to bring these units back into production is not publicly known, some stakeholders expressed a concern that these costs may not take into account the full costs to eventually decommission these units and the long-term cost to store the spent nuclear fuel. The reactivation of these units may also benefit from financing rates that could be significantly less than those rates available to developers of new cogeneration facilities.

As discussed in the previous section, a possible government action to address this barrier is to ensure that the costs to bring these units back into production include the full costs associated with the long-term cost of storing spent nuclear fuel.

5.1.3 Market Power of OPG

Although the Electricity Competition Act and the Market Power Mitigation Agreement (MPMA) seek to reduce the market power of OPG, the company could retain a dominant position in the electricity market for a number of years after the market opens. This presents a potential barrier to the future utilization of cogeneration in a number of ways. 

The MPMA itself has been seen by some as a barrier to entry. It sets a revenue cap of $38 per MWh on 90% of OPG’s capacity. It also explicitly allows OPG to take actions to ensure that the market price comes up to this cap. It is possible that the cap will also become a floor, as OPG uses its market power to prevent the price from rising above the cap on average. As the results of this project show, many potential cogeneration projects cannot achieve a LUEC below $38 per MWh. Setting this price as the wholesale market price, therefore, may preclude these projects from entering the market.

On the other trend, it is possible that market prices will be higher than $38/MWh. Prices in the US mid-West, which averaged $55 Cdn/MWh in 1999, could exert upward pressure on the Ontario price and bring the competitive generation price well above $38 per MWh, although Ontario consumers will benefit from rebates on about 75% of their energy use.

There is also some concern on the part of stakeholders that OPG may offer heavily discounted rates to owners of potential large cogeneration facilities to ensure that OPG retains them as customers and keeps their resulting load base. 

One way to address this barrier is to instruct the Market Surveillance Panel of the IMO to monitor OPG for entry-preventing behavior like that described above.

5.1.4 Market Rules

Although the Market Design Committee was careful to try to ensure that all potential competitors would be treated fairly, stakeholders expressed concern that some aspects of the Market Rules could act to the detriment of small generators, including cogenerators. 

One example is the amount and frequency of information that generators are required to provide to the IMO. To offer supply in the market, they must place offers for the entire day ahead, in hourly intervals, with updates several times a day. Smaller generators may find this information burden onerous.

Under the Market Rules as currently proposed, very small generators (under 1 MW) do not have to meet these information requirements.

5.1.5 Standard Supply Service Code

The Ontario Energy Board’s Standard Supply Services Code (SSSC) effectively places restrictions on the sources from which monopoly distributors can buy electricity for their standard service
 customers. They are allowed to buy only from the spot market or from contract suppliers after an open bidding procedure. Provisions for SSSC are important because it is expected that, especially in the period just after market opening, a large fraction of the total electricity sold to consumers will be under standard service supply.

At the time of the Workshops, the SSSC was understood to allow only spot market purchases. Stakeholders noted that a projected cogeneration plant with electricity in excess of its host’s needs will want to sell the electricity as merchant power. Many developers would prefer to have forward contracts for the some or all of that power, both to reduce their risk and to help in their financing. Stakeholders were concerned that one of the most natural markets for such power was removed.

These concerns may have been mitigated by the ability of the distributors to conduct open bidding for supply contracts.

5.1.6 Cost of Cogeneration Technology

Although advances continue to be made in cogeneration technology that result in lower costs per unit of power produced and/or increased efficiency, the cost remains too high for some applications. Future efficiency improvements can result in lower costs per kWh of electricity that is generated.

As with most technologies, stakeholders expected that this barrier will be reduced if the market demand for cogeneration technology increases in the future. This increased demand will lead to further investments in R&D and larger, more efficient production facilities which, in turn, would lead to higher operating efficiencies and lower cost for the equipment.

This is not a market barrier, as we have defined it here. It is a true cost factor which affects the economics of cogeneration projects. Governments can reduce costs through tax or other policies.

5.1.7 Undervaluing of System Reliability

Cogeneration represents a distributed generation approach to power generation and distribution that is inherently more reliable than a small number of very large plants that depend on a large transmission system to transport the power to where it is required. Stakeholders noted that at the present time, there is no recognition in the pricing system for this increased reliability. 

A remedy for this barrier would be to have locational pricing for electricity. Then generation located inside areas formed by transmission constraints would receive a locational premium. The Market Design Committee recommended that the IMO track locational prices in the first 18 months of the competitive market, and recommend a form of locational marginal pricing after that time. Following that recommendation would remove this barrier. 

5.1.8 Cost of Back-up Electricity

In order to maximize system reliability and meet peak demand, most facilities operating cogeneration systems will also want at least the ability to purchase electricity from an external supplier. While the actual cost of the additional electricity would presumably be at a competitive rate for the amount purchased, stakeholders are concerned that the transmission and distribution charges could be set so high that they prohibit investment in the cogeneration facility. 

5.2 Institutional Barriers

Several institutional barriers relate to information and contracting costs.

5.2.1 Reluctance to Make Long-Term Commitments

Stakeholders felt that senior management of owners of many of the most attractive potential cogeneration sites with a sufficiently high steam and electricity demand are reluctant to make the long-term commitment required to construct a cogeneration plant. This reluctance is particularly large at this time as the electricity market has not yet opened, the new market rules are still under development and the future price of electricity that can be purchased on the open market is unknown.

This barrier will be partly overcome as fair and equitable market rules are developed and after the market has been operating for a few years.

5.2.2 Competition for Limited Funds and Senior Management Attention

Stakeholders noted that senior managers compare the returns/pay back period of potential cogeneration facilities against other potential capital projects. Other projects may have high potential returns and fast payback periods compared to the construction and operation of a cogeneration facility. Related to this issue is the senior management time that is required for any major capital investment.

The solution to these barriers lies in the fact that if cogeneration is or becomes more cost effective than the current power supply options, those companies that do begin to employ it will derive financial savings compared to their competitors and thus gain a competitive advantage. 

5.2.3 Attitudes of Senior Management

Related to the first two institutional barriers are attitudes of senior management of the most attractive potential cogeneration sites. Stakeholders suggested that these attitudes are based on the fact that power supply has not been a part of their core business, electricity has been provided in the past by one utility, and that power supply has not typically been viewed as being as important as other factors impacting the company.

This barrier will never be completely overcome, as power supply will typically not become a core component of most business. In the longer term, if energy prices rise and economic alternatives such as cogeneration become more wide spread, it can be expected that the relative importance of power supply might increase.

5.2.4 Lack of Information, Understanding and Confidence

Although not a new technology, stakeholders noted that there is generally a lack of information, understanding and confidence in cogeneration technologies both by potential users as well as investors. This barrier results in the need by both potential customers and investors to spend the time and cost to inform themselves about this technology. Similar information costs are not incurred if power is simply purchased from an independent third party.

Information costs may be one of the most important institutional barriers. All three of the above barriers effectively relate to information costs. For many potential cogeneration hosts, energy is a relatively small fraction of their total costs, overshadowed by materials or labor costs, for example. To understand the cogeneration opportunity, each firm’s management must spend time developing expertise. 

Well-functioning markets can mitigate this barrier. In a functioning market, if there is an opportunity to save money cost-effectively, the opportunity will be taken. In this case, the information each firm would need is similar. Even if it is not cost-effective for the management of each potential host firm to acquire this information itself, it probably will be cost-effective for a specialist firm to acquire the information and sell it to the host firms. The specialist firms could readily go further than providing information in advance on costs; they could operate the cogeneration facility as well, keeping within themselves the information and management capability that they can apply in several places, while the host company might only apply it once.

An effective way to overcome these information cost barriers may be to promote (or ease) the formation or entry into Ontario of specialist energy information and operation firms.

5.2.5 Early Stage in Development of Industry of Facility Owner/Operators

There are currently relatively few owner/operators of cogeneration facilities in Ontario. These are the specialist firms referred to in section 5.2.4. Stakeholders feel a more mature industry will be required in order to realize the full potential for cogeneration in Ontario. 

The development and maturing of this industry will proceed as this technology becomes more widely spread.

5.2.6 Local Resistance to Siting of New Facilities

Although the siting of cogeneration facilities does not seem to have been a major barrier so far, stakeholders feel it remains an issue that should be closely monitored. It is important to note that local opposition is much less likely for a cogeneration facility than for a merchant plant built to generate electricity exclusively as the cogeneration plan is typically located where there is an existing steam demand and thus an existing boiler. The cogeneration facility is thus merely replacing an existing boiler.

Any local concerns that may arise should be overcome, as residents become more familiar with the technology. It may also be useful to ensure that environmental groups with a provincial overview of the electricity system can provide their perspective on the relative merits of cogeneration.

5.2.7 Transmission Infrastructure

In choosing a location for a new generating facility, investors in merchant plants are free to go anywhere they can acquire land and an adequate fuel supply. Cogeneration investors are limited to locating at the sites where there is simultaneous demand for heat and power. 

Stakeholders emphasized that the design of any cogeneration installation is very specific to the characteristics of the site: the size of the electricity load, the size of the heat load, and the time patterns of their usage (the load durations). In many cases, a cogeneration facility which can meet the heat load efficiently will produce more electricity than the steam host requires. For the cogeneration application to maximize value, and perhaps even to be economic, it requires access to the electricity market for the surplus power. Access to the market will be provided in the coming competitive environment. 

However, some potential cogeneration projects may be located within an area defined by transmission congestion, potentially limiting excess power sales or reducing their value. 

5.2.8 Interconnection Requirements and Costs

Stakeholders reported that some local utilities, particularly the smaller ones, have in the past imposed unnecessarily high technical requirements that a cogeneration facility would have to meet to sell them their surplus electricity or to connect for backup power. Such requirements may severely impact the economic feasibility of those cogeneration facilities which generate electricity that exceeds their own requirements or which require back up from local distribution companies.

This barrier can be addressed by setting a province-wide interconnection standard, or through regulatory challenge of the requirements.

5.2.9 Lags in Equipment Availability

World demand for new electricity generation facilities is currently quite high. As a result of past experience with cycles of high and low demand, producers of generation equipment have been reluctant to ramp up output sharply. Therefore, the lag between order and delivery of new generation equipment, particularly large turbines, has lengthened.

This barrier will only be overcome as more production capacity for the manufacture of this equipment is introduced and the required equipment become more readily available.

Regulatory Barriers

5.2.10 Transmission and Distribution Pricing

Stakeholders were concerned that the transmission pricing tariff proposed by Ontario Hydro Networks Company could create a significant barrier for some potential cogeneration projects. This concern has been reduced by the Ontario Energy Board’s recent decision in the transmission pricing case. It rejected the OHSC proposal to bill new embedded generators for the full transmission tariff. Instead, new embedded generators will pay only for the fixed connection and transformation charges of the system, not for the cost of network operations. 

In addition, the Board accepted that generators below 1 MW not be subject to load billing for any component of the transmission charge.

5.2.11 Environmental Assessment and Approval

As a relatively low emission technology, stakeholders stressed that it will be important to ensure that potential cogeneration projects are reviewed efficiently and promptly, particularly the smaller sized plants. 

The Ministry of the Environment’s new proposed environmental assessment requirements identifies three categories of projects: 1) those that require an individual environmental assessment; 2) those that would require a screening process; and 3) those that that would not require approval under the Environmental Assessment Act. The Ministry is in the process of seeking stakeholder views on what types of projects should be placed in each category and appropriate threshold levels.

5.2.12 Assets Included in Class 43

The federal government allows preferential tax treatment for certain assets that are part of a cogeneration facility. These assets are defined under Class 43. Stakeholders noted that they currently do not include all the assets associated with a cogeneration facility and require a heat rate that may be hard for smaller cogeneration units to attain.

5.2.13 Proposed Power Engineers Regulations

In the summer of 1999, new regulations were drafted to replace the sections of the Operating Engineers Act that stipulate the conditions under which a full-time, licensed operator was required for stationery boilers. The proposals in the new Power Engineers Regulations would require these operators for all steam turbines over 75 kw. The Operating Engineers Act did not include requirements for steam turbines and required an operator for steam boilers over 13,000 lb/hr or about twice the size of the 75 kw proposed in the new regulations.

Stakeholders were concerned that this requirement, if adopted, would have a very detrimental impact on the cost effectiveness of smaller cogeneration plants in the 75-150 kw size range.

Meetings between the concerned stakeholders and those responsible for the Act could move this problem towards a reasonable solution.

5.3 Barriers With No Apparent Policy Approaches

5.3.1 Uncertain Future Natural Gas and Electricity Prices

One of the features of a competitive market is that prices are not controlled and thus future prices will remain uncertain. This barrier has recently been exacerbated by the “North Americanization” of the gas market. Due to the large increase in gas transmission capacity coming on stream in late 2000, a larger volume of natural gas from Canada’s western sedimentary basin will have full access to US gas markets. This and other factors resulted in gas price increases in 1999. It is not yet clear how much of these gas price increases are a result of fundamental market changes and how much are a result of short-term factors such as weather and storage levels or medium-term factors such as low levels of exploration and development activity.

As the physical and market infrastructure for gas matures, gas price volatility may decline. On the other hand, a more actively traded market could become more volatile, especially over short periods of time.

This barrier is related to the informational barriers and to the familiarity of management with management of market risk of various kinds. Installing cogeneration can reduce a company’s exposure to gas prices or raise it, depending on how fuel supply contracts are handled and on what the non-cogeneration electricity supply options are. It can also reduce a company’s exposures to extremes of electricity market prices. As managements become more sophisticated in managing risk, this factor will become another part of the market consideration.

5.3.2 Availability of Steam/Low Grade Heat Hosts

Whereas access to electricity markets had been the prime barrier to cogeneration projects in the past, the availability of steam/low grade heat hosts is now a barrier to greater utilization of this technology.

Appendix A

Gas Price Report

Delivered Natural Gas Price Forecast for Ontario

Current Prices

Current Delivered Prices in Ontario 

Current delivered prices for system gas in Ontario reflect contracts made some time ago. Delivered prices are lower for higher delivery volumes due to lower distribution costs. In October 1999, Firm Service Delivered Prices were as given in the table below.

500 GJ/Month

5000 GJ/Month


Toronto

$5.73 per Mcf

$5.57 per Mcf
Sudbury

$5.01 per Mcf

$4.13 per Mcf
Sarnia


$5.70 per Mcf

$5.40 per Mcf

(Source: Canadian Gas Price Reporter)

Current Border Prices
The October average price at Empress for a 1-year contract is $3.44 per Mcf. This price is well above a comparable price from a year ago. The August field price in Alberta was up by almost $1.00 per Mcf from the previous year. 

Recent Price History
The Alberta border price has more than doubled since 1995. The average 1995 Alberta border price was C$1.21 per MMBtu; the average price for the first ten months of 1999 was C$2.89 per MMBtu. The trend has been steadily upward from July to October, which is consistent with usual seasonal patterns, but the growth has been more rapid than in past years. 

This price increase has been due to two factors: an increase in the price of gas in North American markets generally and a narrowing of the differential between gas prices in Canada and gas prices in the United States. The average differential in 1995 between the NYMEX price and the Alberta border price was over C$1; in 1999 to date, the average differential was C$0.40. 

Gas prices have been increasing in the United States and Canada since the spring of 1999. After strong growth from May of 1999, Canadian prices peaked in September and fell noticeably in October. Monthly gas prices can be volatile. In the twelve months to October, 1999, monthly average prices ranged from C$2.32 to C$3.61 per MMBtu. 

Canadian domestic demand has grown, but not by enough to account for the price increase. Improved transportation facilities have brought the Canadian gas prices closer to US prices. 

Transmission Tolls 
The current firm transmission toll for TCPL is about C$.99 per Mcf from the Alberta border the Toronto City gate. 

Distribution Tolls

The current lowest charge on the Enbridge Consumers’ Gas system for large users in the off peak periods is about $2.15, including charges for storage and balancing. They estimate that a generation plant of 100 MW or more, operating on a gas load factor of about 80%, would pay about $0.40 per Mcf for distribution, including charges for transportation and some storage and balancing. This rate is significantly below the $0.55 per Mcf rate, not including storage and balancing, for their largest industrial customers. It represents an attempt by Enbridge to keep generators from bypassing the distribution system. 

Delivered Price Forecast – Base Case

Alberta Border Price 

Recent price forecasts are available from several sources, including the US Energy Information Agency (EIA) and the National Energy Board (NEB)
. However, most of these forecasts did not anticipate the sharp upward movement in gas prices in the second and third quarters of 1999, so they are already out of date. For example, the NEB has two forecast cases. The Alberta gas prices are $1.82 and $2.50 per Mcf., and the US prices are C$3.00 and C$3.75, in 2010. The highest of these prices are below current prices in both countries.

The question for this price forecast is whether recent prices imply consistently higher prices in the future, whether they are normal variance around an unchanged trend, or whether they represent an earlier move to the forecasted level. The base forecast assumes that the current prices are a temporary upward swing, but that swing is relative to a higher future base price level.

For the base case forecast, the year 2000 price is derived from current market information as received from the Canadian Gas Reporter and from conversations with energy analysts in Alberta and Ontario. The forecast growth rates are based on a consensus forecast growth rate from four sources: the EIA, Gas Research Institute (GRI), Standard and Poor’s/McGraw Hill, and WEFA.

Current forward Empress prices are about at the level forecast above for 2010. It is expected that prices will fall in 2000, as more supply comes on stream, and then rise gradually as increased demand, especially from new gas-fired generation in the United States, takes the supply up. The forecast is therefore based on an Alberta border price of $3.00 per Mcf in 2000, escalating at 1% per year for the next five years and 1.7% per year for the following five years. 

After 2010, the rate of price increase continues to accelerate. It is set at 2.4% per year. This is the average price growth rate of Case 1 and Case 2 of the NEB Report. Using these growth rates, the price of Empress gas reaches $4.35 per Mcf in 2020. This price is about $0.90 above the current price, and represents overall an average growth rate over the entire period of about 1.2% per year from current levels. 

The pattern of price growth in the NEB forecast is opposite to that in the EIA forecast. in the NEB forecast, prices grow more slowly in the early years, accelerating to a rate of over 2% p9er year in the later second decade of the forecast. in the EIA forecast, prices grow more rapidly in the early years, decelerating to 1% per year or less for the second decade of the forecast for all of the forecast cases (except one case for one five-year period.)

Transmission Toll Forecast
There is currently excess gas transmission capacity, resulting from recent TCPL capacity expansions. The excess is expected to increase, with the completion of the Alliance pipeline to Chicago and the probably construction of the Vector line from Chicago to Dawn, Ontario. These will create competitive downward pressures on TCPL rates, until increased gas shipments take up the capacity. 

Beyond this immediate period, it is expected that there will continue to be competitive pressure on pipeline tolls. Given the more open environment for new pipeline investments, response to actual or impending transmission capacity shortages seems to be robust. Further, the monopoly pipeline activities are likely to come under some form of Performance Based Regulation (PBR), which will put increased downward pressure on their costs and rates.

PBR is becoming the first choice of regulators for utilities in restructured competitive markets in North America. It provides better incentives to regulated utilities to reduce costs. While PBR has not yet been applied to gas transmission pipelines in Canada, the expectation is that it will be adopted within the next 5 years.

The combination of competitive pressures on price and PBR pressures on cost lead to the forecast of falling transmission tolls. The forecast gas transmission toll declines steadily, at a rate of just under 1.4% per year for the first 10 years, to arrive at a level of C$.85 per Mcf by 2010. For the following 10 years of the forecast, pipeline tolls fall at a somewhat slower rate, 0.5% per year.

Distribution Toll Forecast
The forecast varies for large and small customers. The current rates for large customers represent significant price discrimination in favor of large users. The discrimination is based at least in part on the potential ability of large users to bypass the distribution system and connect directly to gas transmission. While such discrimination is expected to continue, the forecast shows a mild degree of reduction in its extent. 

For the large users, as for large potential cogeneration plants, the forecast assumes that distribution rates will stay constant in real terms, implying gradual increases in nominal terms. The forecast differentiates between rates for large plants and medium sized one. The toll for large users, plants above about 50 MW, is forecast to remain constant at a rate of $0.40 per Mcf. For smaller plants, around 10 MW, the forecast has a distribution rate above that for the large users, but well below that for smaller commercial users. The distribution rate assumed here is $0.80 per Mcf.

Much smaller cogeneration installations would be expected to pay the residential rate. A generator below 1 MW, for example, might not even qualify for the commercial rate. The current trend in residential consumption of natural gas is downward, as a result of significant increases in average efficiencies of home heating systems. With the resulting excess capacity, there will be little upward pressure on distribution rates due to the need for new investment. On the other side, there will be continuous downward pressure from PBR. These rates, therefore, are expected to move downward steadily. The rate of downward movement reflects the potential for productivity improvements. For the first ten years, the distribution rates trend down by about 2.2% per year; for the succeeding 10 years, they fall by about 1.5% per year.

Upper and Lower Case Forecasts

The upper and lower cases are derived entirely from alternative forecasts of Alberta border prices for gas. The transmission and distribution tolls do not vary between cases. The focus of this study is on the impact of gas prices on the potential for cogeneration in Ontario. Varying gas prices allows enough price spread for this analysis.

The cases are based on the two cases of the recent National Energy Board forecast. That forecast analyzes two cases. In that forecast, Case 1 represents a combination of low cost supply and current demand trends, to produce a higher quantity of energy demanded. Case 2 represents a combination of current supply trends and accelerated demand efficiency, to produce a lower quantity of energy demanded. Case 1 can generally be expected to produce lower prices and Case 2 to produce higher prices. However, the NEB chose them for their impact on demand, not price; the highest price would be produced by a combination of current supply trends with current demand trends, and the lowest by a combination of lower cost supply and more efficient demand. For the purpose of this forecast, therefore, the two cases allow a reasonable test of the assumptions, without creating extremes.

The National Energy Board report predates the natural gas price increases of later in 1999. Using it therefore requires some assumptions about how to match its forecasts to later events.

Low Price Case

The low price case assumes that the price history since the publication of the NEB report represents normal variance around the prices in the case. For this case, the gas price in 2010 is taken as the 2010 price from the NEB Case 1. That price is significantly below the assumed 2000 price. To reach the predicted level, the price is forecast to fall for the first ten years. Although the price probably will not fall smoothly over that period, the low price case smoothes the drop, in order to avoid the need to predict a specific dynamic pattern. The rate of decrease was calculated as the rate needed to reach the NEB forecast price by 2010; it is a real decline of 3.5% per year.

After 2010, the low price case forecast uses the NEB’s forecast growth rate from 2010 to 2025 for the period from 2010 to 2020.

High Price Case

The high price case is also based on the NEB forecast, but it assumes that the forecast price in 2000 forms a new basis for price increases. The case is therefore derived by applying the forecast price growth rates from NEB’s Case 2 to the assumed price in 2000. This produces prices that are notably higher than those in the base case. The growth rates are those for the Alberta border price in two ten-year blocks: from 200 to 2010, and from 2020 to 2020.

The two cases are not symmetrical. The low price case is farther below the base case than the high price case is above it. This is in keeping with the current sentiment among gas price forecasters, who generally believe that the risk in gas prices, at least for the next five years or so, is downward. Higher oil and gas prices have stimulated exploration and development activity in Canada, which is expected to increase supply and bring current prices down.

[image: image22.wmf]Economic Potential at $50/MWh Electricity Price

Project Location

Market Segment

Electrical 

Capacity 

(MW)

Probability of 

Proceeding

Identified 100-250 MW

Ottawa/Carlton Pulp & Paper

nug

153

L

GTA

nug

150

M

East. Ont. Pulp & Paper

nug

180

M

NW Ont. Pulp & Paper

nug

165

L

NW Ont.Pulp & Paper

nug

180

L

Totals

5

828

Identified :250 MW  and larger

GTA Pulp & paper

ind

250

H

Niag. Penn Pulp & Paper

ind

350

M

West. Ont.

nug

550

H

Niag. Penn.

nug

350

M

Totals

4

1,500

Total economic potential

2,328


[image: image23.wmf]Table 4.1

Cogeneration Potential in Ontario

Sensitivity Analysis based on 250MW Combined Cycle Cogeneration Case (CCC250 )

Parameter Changed

Changed

LUEC without

LUEC with

IRR

Thermal Credit 

[1]

Thermal Credit 

[2]

(Cdn$/MWh)

(Cdn$/MWh)

(%)

Base Case

46.72 Cdn$/MWh

50.82

46.72

13.00

Electricity Rate

38.00 Cdn$/MWh

-

-

N/A 

[3]

45.00 Cdn$/MWh

-

-

0.74

50.00 Cdn$/MWh

-

-

25.47

Heat Rate

-5%

49.13

45.03

13.00

-10%

47.44

43.34

13.00

Capital Cost

-5%

50.21

46.12

13.00

-10%

49.61

45.52

13.00

Note:

[1] 

LUEC is based on the cost of steam equal to zero Cdn$/klb

[2] 

LUEC is based on the cost of steam equal to 7.51 Cdn$/klb

[3] 

IRR in this case is not available since all the net cash flows along the study period are negative.


[image: image24.wmf]5 yr 

5 yr 

5 yr 

YEAR

$

AAGR

$

AAGR

$

AAGR

2000

3.00

3.00

3.00

2005

2.51

-3.50%

3.15

1.00%

3.49

3.10%

2010

2.10

-3.50%

3.43

1.70%

4.07

3.10%

2015

2.34

2.20%

3.86

2.40%

4.65

2.70%

2020

2.61

2.20%

4.35

2.40%

5.31

2.70%

LOW CASE

BASE CASE

HIGH CASE



FORECAST GAS PRICES

Alberta Border

(All prices in $2000/Mcf)


Appendix B

First Workshop Report

POTENTIAL FOR COGENERATION IN ONTARIO:

NOTES FROM DECEMBER 9, 1999 STAKEHOLDERS WORKSHOP

Prepared for

Energy Policy Branch

Ontario Ministry of Energy, Science & Technology

By

Hagler Bailly

In association with

AGRA Monenco

And

Lourie & Love Environmental Management Consulting

January 31, 2000

1. INTRODUCTION

The main purpose of this report is to summarize the discussions that took place during the half day Stakeholders Workshop that was organized December 9, 1999. It also includes copies of the material distributed at this workshop so that it can be sent to those who were not able to attend but expressed interest in being kept informed.

The purpose of the Workshop was to seek the views of selected stakeholders on the opportunities for cogeneration applications in Ontario and on the major barriers that may prevent wider utilization. This workshop was part of a project that the Ministry of energy, Science and Technology is currently undertaking, in cooperation with the Ministry of Natural resources and the Ministry of Economic Development and Trade, to evaluate the potential for cogeneration in Ontario.

A list of 32 potential participants were identified, representing the following five major categories:


Current cogeneration plant operators


Potential operators/developers


Equipment manufacturers


Financial consultants


Environmental non-government organizations

The list of invitees to this workshop is included in Section 5 of this Appendix.

2. SUMMARY OF PLENARY SESSION

Doug MacCallum of the Ministry of Energy, Science & Technology began the workshop by welcoming all participants. He noted that this project was part of the Ontario government’s response to the challenge of reducing Ontario’s greenhouse gas emissions. He also noted that a number of the recently published federal “Issue Tables” that had assessed a wide range of opportunities to reduce CO2 emissions had referred to cogeneration as one of the technologies that offer the potential for significant emission reductions.

Peter Love of Lourie and Love began by noting how pleased he was to see such a good turn-out for this workshop, particularly in light of the relatively short notice and the time of year. He also noted that the participants represented a broad range of interests and felt that this would be very useful during the discussions. He then briefly reviewed the Agenda for the workshop (included in Section 5), noting that the project team planned the event to maximize the time that participants could spend discussing the key issues in three breakout groups.

He then summarized the workshop objectives, which were:


To seek views of representatives from major stakeholders on:



Most attractive cogeneration applications in Ontario



Major barriers that may prevent wider utilization

He also noted that the focus of the workshop would be on seeking views of participants during the breakout group discussions. He suggested that in addition to discussing the two above-noted issues, these breakout groups might also want to address the key question “What would it take for your organization to consider proceeding with a cogeneration project”. Based on a brief discussion of this question statement, it was generally agreed that many organizations are already “considering” such projects and that a better phrasing of this question might be:

What will it take for your organization to proceed with a cogeneration project?

Scott Stevens of Energy Ventures Group, representing AGRA Monenco, then briefly summarized the initial cost estimates of alternative cogeneration technologies that had been developed for this project. The capital, O&M, fuel, levelized tax and resulting Levelized Unit Electricity Cost (LUEC) before and after the steam thermal credit for 8 medium-large units (>10 MW) and 19 small units (<10MW) were summarized on two tables; these tables are included in Appendix B of this report. The delivered prices for natural gas to 2020 for three categories of plant sizes (>50 MW, 10 MW and < 500 kW) under three scenarios (Low, Base and High), in $2000/Mcf were also presented and are included in Appendix A of this report.

Workshop participants who had comments on these assumed costs were asked to contact Scott directly after the workshop as it was felt that such discussions would be better conducted on a one-on-one basis.

Mitch Rothman from Hagler Bailly, who is the Project Manager for this project, began by thanking participants for taking the time to provide the study team with their thoughts and insights on the issues associated with cogeneration. He then briefly reviewed an initial list of fourteen potential barriers to cogeneration; this list is included in Section 5. He emphasized that this list was intended to start the discussion on barriers, was not intended to be comprehensive and that they were not presented in any order of importance.

There followed a general discussion of the barriers to cogeneration; the following were the main points that were raised during this discussion:

1. Limited number of suppliers

2. Uncertainty of prices significant—gas, electricity

3. Uncertainty of supply

4. Uncertainty of nuclear power input

5. Size of project & barriers to small projects

6. Lack of district heating limits steam host opportunities

7. Environmental approval regulations—these require harmonization

8. Access to equipment

9. Market in environmental emission credits; will overcome the environmental externality barrier in favour of cogeneration

10. Ability of financial people to convince CEO’s of benefits / risks

11. Cost of back-up power – will penalize cogeneration

12. Need to treat very small plants inside the meter as a demand management measure; gross vs. net billing

13. Barriers can be divided into short and long term issues

14. Issue of taxation incentives must also be addressed

15. Need to look at emission trading potential and the role that this can play in maintaining a market for CO2 and NOx etc., which may be reduced through cogeneration

16. How to look at a whole suite of pollutants instead of a few?

3. NOTES FROM BREAKOUT GROUPS

The following three sections summarize the main points that were discussed during each of the breakout sessions, as recorded by the facilitators and presented to the workshop when the groups reconvened.

3.1
Group A

Facilitator: Peter Love, Lourie & Love

Greg Allen
Green Energy Coalition

David Bond
Ministry of Economic Development & Trade

Frank Dixon
Westcoast Power

Harry Goldgut
Great Lakes Power

Finn Greflund
TransCanada Energy

Susan Olynyk
Dofasco

John Welch
General Electric

Aqeel Zaidi
Union Gas

This group appeared to spend more time discussing the first issue (most attractive cogeneration opportunities) than the other two groups. 

Breakout members first briefly introducing themselves, noting their interests in cogeneration. During this opening discussion, the following barriers to cogeneration were noted, many of which relate to the future electricity pricing by OPG:

· Uncertainty of future power prices and concern that OPG will do whatever possible to retain their current load

· Artificially low electricity prices as OPG has been allowed to write-off much of its debt

· The real avoided cost of power in Ontario is likely $0.06/kWh, $0.10 for nuclear

· No technology can compete with nuclear if capital costs are written off and there is insufficient provision for decommissioning of plants

· Lack of information regarding cogeneration

· Companies are slow to make major investment decisions in an uncertain environment and require detailed risk analysis before proceeding

· Senior management do not see cogeneration as “a big deal”

· Large industries are not in the business of making power themselves and thus might prefer to contract to third party

· Financing of cogeneration projects currently requires more equity and thus higher returns as amount of debt financing is limited

· Load factor could be a critical issue, particularly if Bruce A units come back into production

· There is currently no capacity shortage in Ontario but there is a capacity market in New York

· Availability of a sufficient steam demand will be critical for future facilities; availability of electricity demand was primary limitation previously

Most Attractive Opportunities 

The group then discussed the ideal opportunities for cogeneration. It was generally agreed that the larger plants (>200 MW) that offered significant economies of scale would be the most attractive. As it was generally agreed that a large steam demand was required, the following were identified as the most attractive potential applications:

· Integrated iron & steel mills - 4 in Ontario

· Forest products industries

· 32 pulp & paper mills in Ontario

· some are Forest products industries

· beginning to use less natural gas due to process changes (TMP mills primarily electricity and steam demand)

· most inexpensive biomass is already being recovered

· new MNR regulations preventing landfilling may result in additional sources of biomass

· some older plants are looking at major capital equipment replacement projects

· no developers seem interested in this market at this time

· study of biomass potential by Union Gas available upon request

· Petro-Chemical plants (Sarnia)

· Institutions (eg hospitals)

· major advantage is that they would get to keep resulting costs savings

· (not the case with most commercial buildings where costs passed onto tenants)

· Municipalities (sewage treatment, district heating/cooling, municipal waste)

· Commercial buildings – only when they are grouped together as clusters

Future Electricity Pricing
The future prices for electricity was identified as a key issue. Although the pricing shortly after market opening may be difficult to predict, this group agreed unanimously that in the longer term (2 years), industrial electricity prices in Ontario would be higher than they are now. It also agreed that this will come as a rude awakening to many large electricity consumers who have been actively advocating an open, competitive electricity system in Ontario as they believed that this would lead to lower electricity prices. This will represent a major opportunity for cogeneration.

Major Threats to Cogeneration
The return of up to 5 GW of currently idle nuclear capacity in Ontario was seen as the largest threat to cogeneration.

This threat could be reduced if the operators of these facilities were forced to include the full costs of decommissioning and liability associated with long-term storage of nuclear wastes 

Most Important Controllable Barriers
· Net billing, locational pricing and uneconomic by-pass

· Emission reduction credits, particularly in non-attainment zones, for NOX and perhaps CO2
· Harmonization of permitting between Canada and the US

· Confidence, experience and financial information on cogeneration projects

· Trust/comfort level between consultants, developers and end-users

· Clarification of transmission charges to alleviate congestion and encourage more generation where needed (eg Alberta’s locational credit system)

· Competition transition Charge – how much is it? How will it be applied? Gross/net basis? At consumption or generation level?

Uncontrollable Barriers
· Market uncertainty re nuclear facilities

· Potential for export sales to US (higher in summer, lower in winter as US utilities are summer peaking 

· Lower prices in Quebec and Manitoba (limited by current interconnections)

3.2
Group B

Facilitator: Mitch Rothman, Hagler Bailly

Peter Heffernan
Rolls-Royce

Ed Kress
Great Lakes Power

Doug MacCallum
Ministry of Energy, Science and Technology

Robert McLeese
Access Capital

Scott Stevens
Energy Ventures Consulting

Dale Struthers
O&Y Enterprise

Ian Stewart
O&Y Enterprise

Paul Vyrostko
Northland Power

Henry Wegiel
Dofasco

This session first considered a number of overall categories of barriers to cogeneration. We elaborated on the sources of those barriers, and then tried to identify which of them were likely to be long-term influences. We also tried to identify a list of major short-term issues.

The categories of barriers that were identified were:

· Inability of host to commit

· Commercial and regulatory risk

· Transmission rates

· CTC

· Regulatory policy

· Information 

· Tax policy

· Electricity price uncertainty

In the list below, each of these categories is headed in bold. Those that were identified as long-term issues have the abbreviation LT in the right side of the listing. 

Inability of host to commit 

WHY?

· No long-term PPAs

· No gas price certainty
LT
· No price history for the revenue stream

· Customer inability to commit long-term

· Uncertainty of spark spread 
LT
· Discomfort with energy as a long-term investment area for a manufacturing company “This is not our core business” 
LT
· Lack of board-level focus on energy/electricity

· High hurdle rates for core business

· Reluctance to take risk in a non-core area

Commercial Risk vs. Regulatory Risk

· Manage commercial finance issues (eliminate regulatory risk, can negotiate commercial risk)

· Can’t manage regulatory risk 
LT
· Regulatory risk may/may not go away (lessen)

Transmission Rates 

· Gross billing 

· Some matters are policy, not regulatory 
LT
· E.g. “Customers pay for costs they incur”

· Penalties for cogen

· complexity of proposed rate structure

· congestion pricing

· why is OHSC apparently against new generation?

CTC
LT
· How collected?

· What basis?

· Who Pays?

· How will generation affect it?

· (Should interruptible customers pay it?)

· Will CTC be applied equally to all competitors?

Regulatory Policy
· Firm government commitment to a market reduces risk 
LT
· Do proposals promote objectives of the act?

· Cost imposition for transmission system expansions 
LT
Beneficiaries?

All system users?

· Uncertainty of market access for merchant components

· Uncertainty of emissions rules

· Uncertainty of environmental assessment process

· Uncertainty on cross-border policy harmonization (trading, labelling)

· Uncertainty of impacts of environment and other cross-border regulation

Information
· Unequal access to historical information

· Withdrawal of previously available information

Tax Policy
· Class 43 lack of credit for by-product fuels 
LT
· Municipal tax (uncertainty about treatment of hydro)

· Low value of Class 43 tax treatment

Electricity price uncertainty

· Restrictions on existing NUGs

· Impact of MPMA 
LT
OPGI bidding strategy

Speed of divestiture

Restrictions (or lack) on OPGI behaviour

· Is $38/MWh a cap or floor?

· Nuclear performance 
LT
Who pays rehab costs?

Default supply (SSSC)

Big Short-Term Issues

· Gross vs. Net

· Standby charges

· CTC

· IMO uplift issues

· Lack of market experience/MPMA

· Asymmetry of market information

· High operating cost of cogen compared to price cap

3.3
Group C

Facilitator: Bruce Lourie, Lourie & Love

Bruce Ander
Toromont Power

Frank Bajc
ACTO/CU Power

Rick Greenwood
Ministry of Natural Resources

Mike Kuriychuk
Bowater

James Perry
Ontario Power Generation

Todd Wilcox
Toronto Hydro
Adam White
TransAlta

Phil Wood
Enbridge Consumers Gas

This group focused primarily on discussing the barriers to cogeneration; any possible solutions that were discussed are written in italics.

Three Major Barriers

1) Gross Billing Decision

2) CTC

3) Environmental Regulations

Divide the barriers into:

1) Policy, including market rules

2) Market / Technology

Policy / Market Rules

Big Issues:

· Stranded debt – CTC

· Fundamental conflict in government; as owner, generator, regulator and consumer

· High CTC protects old plants

Possible Solution: 

· Need to look at the level, duration and exemptions from the CTC for highly efficient new plants, as an incentive for developing new technologies and reducing air pollution.

Gross Transmission Billing; a barrier:

· Not based on transmission use

Possible Solution: 

· Allow for net billing—giving fair treatment

Back up power:

· Uncertainty / high costs of connection; leads to monopoly control

· Negotiating technical interconnection

· Role of OEB arbitration is uncertain

Possible Solution:

· Interconnect standards / ruling to overcome this barrier

Imbedded Generation is being treated unfairly; this limits cost choice.

Possible Solution: 

· Overcome this barrier by providing equal treatment / level playing field for imbedded generation
Barrier aggregating thermal load, district-energy, role of municipalities

Timing and extent of locational pricing

Uncertainty re: scheduling of small projects through IMO

Environmental / Climate Change Drivers

· No teeth in climate change policy

· Uncertainty in government response to climate change

· Uncertainty re: emission caps (timing) and trading rules

· Costs / allocation of credits

· Present standards based on point of impingement, not heat rate; this penalizes efficiency

Possible Solution:

· Overcome by setting / clarifying standards that encourage efficient generation

· Favourable tax treatment for high efficiency / low emission

· Common emission standards for new and existing plants

Environmental Approvals:

· Lack of updated process

· Lack of “Green Energy” certification standard

Market / Technology

Time / Cost barrier for smaller plants / projects

Technology / Information

· Focus on development information NOT technical information except fuel cells etc.

· Time / cost barrier

· Local resistance negligible

4. CONCLUDING COMMENTS

The main features of the discussions in each breakout group were summarized by the facilitators. No attempt was made to summarize the many common themes that emerged from these presentations but it was noted that the three groups approached the issues in different ways. Group A spent most of their time discussing the most attractive potential cogeneration applications and divided the barriers into controllable and uncontrollable. Group B focused on discussing short term vs. long term barriers. Group C identified three major barriers and identified the major issues and possible solutions.

During the ensuing discussion, reference was once again made to the fact that future electricity prices will be critical to the success of new cogeneration projects. The Ministry of Energy, Science and Technology was asked to provide participants with the government’s best estimate of future electricity prices. Subsequent to this workshop, the Ministry of Energy, Science & Technology informed the study team that there was no official price forecast. The Ministry suggested that the project team use three electricity generation price levels in the projections: $38, $45, and $50 per MWh.

At the end of the workshop, Doug MacCallum once again thanked all participants for their time and cooperation. He added that all participants (as well as those who were interested but could not attend) would be invited to the next Stakeholders Workshop. This will be held:



Tuesday February 15, 2000

Participants at this workshop will be sent a draft copy of the consultant’s report on the potential for cogeneration in Ontario for their review prior to this workshop. 

5. LIST OF INVITEES, INVITATION, AGENDA AND INITIAL LIST OF POTENTIAL BARRIERS

5.1
List of Invitees

ABB Alstom Power
Martin Lenzin

(403) 278-7111

Access Capital
Robert McLeese
(416) 366-4820

AMPCO (Association of Major 

  Power Consumers of Ontario)
Ken Snelson

(416) 769-8880

ACTO/CU Power
Frank Bajc

(416) 620-1992

BOMA (Building Owners and

  Manufacturers Association)
Ian Stewart

(416) 862-6005

Boralax
Yves Rheault

(514) 363-5130

Bowater
Catherine Cobden
(819) 643-7200

Canadian Pulp and Paper Assoc.
Lucy Veilleux

(514) 866-6621

Dofasco
Tom McGuire

(905) 544-3761

Enbridge Consumers Gas
Phil Wood

(416) 495-8350

GE Power Systems
Glen Kennedy

(416) 858-5314

Great Lakes Power
Harry Goldgut

(416) 956-5139

Green Energy Coalition/Sierra Club
Greg Allen

(416) 488-4425

Hospital for Sick Children
Gregory Dick

(416) 813-5171

IPPSO (Independent Power 

 Producers Society of Ontario
Jake Brooks

(416) 322-6549

Northland Power
John Brace

(416) 962-6262

Ontario Clean Air Alliance 
Jack Gibbons

(416) 923-3529

Ontario Lumber Manufacturers
Agnus Rocha

(416) 367-9717

Ontario Power Generation
James Perry

(416) 592-5318

Pollution Probe
John Welner

(416) 926-1907

Pratt & Whitney
Ted Traynor

(905) 564-4135

Probyn & Company
Stephen Probyn
(416) 777-2800

Rolls-Royce
Peter Heffernan
(905) 201-0724

Sudbury District Energy Corporation
Brund Pozza

(705) 673-9133

Toromont Power
Bruce Ander

(416) 667-5724

Toronto Hospital
Mike Horn

(416) 340-4800

Toronto Hydro
Todd Wilcox

(416) 542-2588

TransAlta
Barry Chuddy

(905) 869-2162

TransCanada Energy
Finn Greflund

(416) 829-7246

Union Gas
Dave Simpson

(519) 436-4651

University of Toronto
Harvey Krueger
(416) 978-6650

Westcoast Power
Frank Dixon

(416) 499-3676

5.2
Invitation to Workshop

Ministry of Energy, Science & Technology Letterhead)

November 26, 1999

Dear Cogeneration Stakeholder:

I would like to invite you to participate in a half day Stakeholders Workshop on Thursday December 9 from 9:00 to 1:30 at the Sheraton Centre, 123 Queen St. West, Toronto.

The purpose of this Workshop is to seek your views on the most attractive opportunities for cogeneration applications in Ontario and on the major barriers that may prevent wider utilization. The is part of a project the Ministry of Energy, Science and Technology is currently undertaking, in cooperation with the Ministry of Natural Resources and the Ministry of Economic Development and Trade, to evaluate the potential for cogeneration in Ontario. 

The restructuring of the electricity market currently underway in Ontario is expected to remove one of the major barriers to cogeneration projects by allowing access to electricity markets. There are several remaining factors that will be critical in evaluating the likely uptake of cogeneration. We would ask that in preparation for this workshop, you begin to identify what you consider to be the major barriers to wider utilization of cogeneration.

It is our intention to distribute the Notes from this Workshop to all participants. The Ministry’s consultants on this project (Hagler Bailly, AGRA Monenco and Lourie & Love) also plan to facilitate a second workshop in February to review their draft report that will incorporate the discussion at this December 9 Workshop.

Please find attached to this invitation the Agenda for this Workshop and a Confirmation Form. If you have not already confirmed your attendance by phone, please fax back the attached Confirmation Form by December 2 or email your confirmation (plove@lourielove.com). If you are unable to attend, please let us know if there is another representative from your organization that would be able to participate.

We hope that you will be able to participate at this Workshop and thank you for your time and consideration.

Yours truly,

Doug MacCallum

Team Leader, Energy Economics

Energy Policy Branch

5.3
Agenda

COGENERATION STAKEHOLDERS WORKSHOP

Thursday December 9, 1999

9:00 – 1:30

Simcoe/Dufferin Room, Sheraton Centre

123 Queen St. West, Toronto

8:30
Registration, Coffee

9:00 
Welcoming Remarks 

9:10
Review of Workshop Objectives and Agenda

9:15
Outline of Objectives of “Potential for Cogeneration in Ontario” Project 

9:25
Presentation of Initial Cost Estimates of Cogeneration Technologies

9:35
Summary of Initial Identification of Barriers to Wider Utilization

9:45
Questions/Comments

10:00
Bio Break

10:15
Reconvene into Three Breakout Groups

Each to discuss most attractive applications, major barriers to wider utilization and other issues of interest

11:45
Reports from Breakout Groups

12:15
Questions/Comments/Observations

12:30 
Working Lunch/Further Discussions

1:15
Conclusions/Next Steps

5.4
Initial List of Potential Barriers to Cogeneration

The list below is intended to start the discussion on barriers to cogeneration in Ontario. The list is not intended to be comprehensive, nor is it in any particular order of importance. The purpose of the Workshop is to develop a list of factors that the stakeholders see as barriers, in order to allow further analysis of them as the project proceeds.

· User unfamiliarity with cogeneration technologies

· High information costs for energy purchasers to find out about cogeneration

· Arbitrarily short payback periods or high hurdle rates by potential cogeneration hosts

· Difficulty of financing merchant portion of projects

· Local resistance to specific sites

· Uncertainty about transmission regulatory treatment

· Uncertainty about distribution regulatory treatment

· Inability of cogeneration to get payments for contributions to system reliability

· Low commodity prices for electricity

· Scarcity of locations which can use steam or low-grade heat

· Uncertainty of future gas prices

· Uncertainty of future electricity/gas (“spark”) price spreads

· Cost of cogeneration technology

Appendix C

Second Workshop Report

POTENTIAL FOR COGENERATION IN ONTARIO:

NOTES FROM FEBRUARY 15, 2000 STAKEHOLDERS WORKSHOP

Prepared for

Energy Policy Branch

Ontario Ministry of Energy, Science & Technology

By

Hagler Bailly

In association with

AGRA Monenco

And

Lourie & Love Environmental Management Consulting

March 31, 2000

1. INTRODUCTION

The main purpose of this Workshop was to discuss the draft copy of the project report that had been sent out to workshop participants for their review. A list of the invitees to the workshop and the letter inviting them to participate is included in Section 3. 

As with the previous December 15 Workshop, Doug MacCallum of the Ministry of Energy, Science and Technology welcomed participants to the workshop and thanked them for their cooperation.

Peter Love then briefly summarized the objectives of the Workshop and the proposed agenda (copy included in Section 3). He then asked for any comments on the Report of the December 15 workshop which had been sent out to participants; no major changes or revisions were suggested.

Mitchell Rothman, the Project Manager, then summarized the main features associated with the estimated potential for cogeneration in Ontario and there followed a discussion on a variety of points. As these points were further discussed in the breakout groups, they are not summarized here.

Peter Love then summarized the major barriers that had been identified and were discussed in the draft report. Workshop participants were encouraged to review and expand on these barriers in their breakout groups.

Based on the interests of the participants at the Workshop, it was agreed that there would be three breakout groups that would discuss and review the draft report from three perspectives:

Large Plants (>10 MW)

Small Plants (< 10 MW)

Pulp & Paper Industry 

2.
NOTES FROM BREAKOUT GROUPS

The following sections summarize the main points that were discussed during each of the breakout sessions, as recorded by the facilitators and presented to the workshop when the groups reconvened. The fourth section, prepared by the consultants after the workshop, summarizes the major conclusions and next steps.

2.1 Large Plants

Facilitator:

Peter Love


Technical Resource:
Scott Stevens

Terry Vaughan
Access Capital

Frank Bajc

CU Power International

John Welsh

GE Power Systems

Ed Kress

Great Lakes power

Bob Porter

TransCanada Energy

Richard Chan

Union Gas

1.
Economic Assumptions

Debt Rate
2 of 6 preferred working in nominal rates (i.e. 8% including inflation)



other 4 were indifferent



current rate based on risk free rate (6%) plus risk premium (1.8-2%)

Term

25 year term assumed is OK



current tendency is now to shorter term natural gas contracts (3-5 years)



high premium for 10 year gas contracts

Debt/Equity
50/50 for merchant plants



smaller plants will tend to be financed with balance sheet financing



ratio will depend on structure of the project/coverage rates



group suggested running sensitivity using 60/40

IRR

13% a little high; 12% more reasonable



assumes no residual value

Steam

some contracts currently for as low as $2.45



will come down as efficiency assumed in evaluations is increased 



could be 0 to get some projects to qualify for Class 43



could be based on the highest value for steam



could also be based on real avoided cost approach



group suggested that a sensitivity analysis be run using $5.00

Capacity
would certainly be lower for merchant plants, especially peaking plants



for co-gen, will only proceed if it can be run at high capacity



no sensitivity runs required



steam reliability is key concern for all industrial users



might involve leaving existing boilers in place and/or multiple units



assumed that the required reliability was already incorporated into costs 

Other Issues
cost of back-up electricity





What was assumed in this project?

2.
Potential


Group felt strongly that systems <150MW should not be ruled out



costs should be compared to delivered cost (including CTC, T/D, etc.)



delivered cost of electricity could be even higher for smaller users


Group suggested a price/potential chart be developed


Generally agreed that technical potential should start with inventory of boilers



Hydro study and Acres report for MOE about 83/84 were suggested


Guess is that the number of locations >10MW steam demand is multiple hundreds


District Energy Potential



Cdn District Energy Assoc – identified 23 projects across Canada



Note: avoid double accounting potential with potential for small plants

3.
Barriers

Additional barriers that were identified by the group:


Cost of backup electricity


Low subsidized cost of existing district heating projects


Required transmission infrastructure may not be in place in all potential locations


Inexpensive hydro in N. Ontario


Environmental regulatory approvals (subject of MOE workshops)


If caps on other industries in future, should be on net, not gross, emissions


Environmental controls should be no more stringent than on existing units



(e.g. requirement for emissions monitoring on units >25MW) 


First nations issues, including use of “traditional” lands, becoming very important


Discussion of distribution issues should be added to Transmission pricing section 



of draft report


Federal government should be encouraged to expand asset coverage of Class 43



(e.g. more of the infrastructure required for hydro projects)


For smaller plants (<1MW), connection specs by local utilities may be onerous


Note was made of a CERI project currently underway on barriers to district energy

4. Potential Drivers to Increased Co-gen

The group also identified the following drivers which will tend to encourage greater utilization of co-gen:

NIMBY leads to inability to site future large generation plants or transmission 

Economies of scale favour distributed generation


Emerging market for emission credits could become significant

2.2 Small Applications

Facilitator:

Mitchell Rothman

Andrew Amiri

Cummings Ontario

Masoud Almassi
Enbridge Consumers Gas

Bernard Jones

ONGA

Paul Vyrostko

Northland Power

Mike Horn

Toronto General Hospital

Derek Macartney
Trigen Canada

Helmut Krueger
University of Toronto

Frank Dixon

Westcoast Power

The group discussed an agenda, which was then organized into three broad topic areas: Definitions, Drivers, and Barriers.

Definitions

1. There may be a more important break between installations over and under 5 MW than between those over and under 10 MW.

2. Fuel cells for house-size applications are clearly small. But they would still have to meet safety and performance standards.

3. In the market for small cogeneration, the owner can choose the appropriate technology for installation; in the larger applications, the technology is inevitably gas turbine.

Drivers
1. Capital Costs

· Costs are very site-specific

· Are installation costs included in the costs as displayed? What other costs are included, for example, chillers?

· Installed cost of $1200-2000 per kW for reciprocating engine technology is reasonable.

· $1650 per kW is reasonable for a small reciprocating engine.

· But the larger units may not decline in cost as much as is shown, because of quality upgrades. 

2. Operating Costs

· Operating costs for reciprocating engine technologies are usually underestimated. Need to get feedback on that from operators.

· $20/MW is not unreasonable for O&M costs for reciprocating engine technologies.

· $15/MW (as shown in the table) is the top of the range for O&M costs for reciprocating engine technologies.

· Are the O&M costs for small turbines underestimated?

3. Electricity vs. Heat Output

· There is no game without heat

· Or: There is no game without both heat and electricity 

· Electricity sales need peaking rates

4. The Business from the Investor’s Point of View

· The investor has equipment to operate

· Its returns (electricity price) are uncertain

· Its costs (gas price) are uncertain

Barriers
1. Operating Engineers Act

· Proposed change requires on-site engineer for even small turbines

· Does not recognize technology (automatic shut offs)

2. Connection Codes

· Can bring installed cost up to 3x capital costs

· Example: $300 K connection cost for 2x333kW project; killed project

· To protect the small generator from the grid costs $5 K; to protect the grid from the generator costs $300 K; does this make sense?

· Utilities may use codes or stall/delay approvals if they do not want generation

· But most MEUs not the barrier; extent of MEU barrier depends on their regulation and incentives

· Manufacturers can get around this with a pre-engineered package

· No province-wide standard for interconnection; should be set by neutral third party

3. Standards for Installation

· Noise suppression (especially for gas compression)

4. Class 43 Criteria

· Small installations may not be able to attain Class 43 heat rates

5. Emissions Credits

· OPG has a head start on trading emission credits

· How do new generators get credit when they are moving to self-generation from buying electricity?

6. Information Barriers

· Host companies do not want to become utilities

· Need to develop a more mature industry of owner-operators

· Lag in equipment availability

2.3 Pulp & Paper Industry

Facilitator:

Bruce Lourie 

Recorder:

Leah Hagreen

Mike Kuriychuk
Bowater

Dennis Foran

Domtar

Peter Heffernan
Rolls-Royce

Paul Marier

Spruce Falls

Gerry Murray

Strathcona Paper

Susan Shaw

Trigen Canada

Aqeel Zaidi

Union Gas

Assumptions

1. Boiler efficiency assumption too low @ 70%, should be ~80% (for industrial, left on at all times; may be low if facility is turned on and off)

( this will change steam cost #’s; in reality steam value ~$5

2. Efficiency #’s for turbine need to indicate whether lower heating value or higher heating value 

3. Electricity pricing needs to show: 

· on-peak

· off-peak

· delivered

4. Similar to gas tables should be sensitivity table for delivered electricity price (value not cost)

5. Suggestion to look at price forecasts in region (US)

6. Need an electricity price forecast with assumptions **

7. Need to see gas assumptions behind forecast

8. Technology assumptions suggest minimum steam use as heat ( misses the most likely configuration of combined cycle with non-condensing turbine; this should be included

9. Note that report needs to be clear that focus is gas cogen not steam cogen 

(define cogen clearly**

10. Need to consider a variety of commercial operations and clarify what is and what is not included

11. Importance of biomass***

· The importance of biomass for cogen must not be overlooked for the pulp/forest sector; this should be included or qualified, as it has important greenhouse gas implications (being the start to this whole process)
12. Is the focus cogen or generation ( peaking is not cogen

13. What is the discount rate for NPV analysis? Does not look like NPV actually considered. Prefer constant $.

14. Need to see all assumptions in financial analysis

· Interest rates

· Discount

· Tax rates

· Before / after tax assumptions

· Cash flow

15. Report assumes non – by-passable transmission costs (i.e. third party)and is limited by 3.8cent constraint

16. Actual availability for aero-plants >90% (~95%)

Technical Potential

1. 1987 Acres report is the best source of technical potential in Ontario; should be used as a good cross-check

2. clarify definition of technical potential; the report does not use true “technical” potential, but one that has an economic screen

3. who’s “probability” assessment, how was it derived, how was it assigned, what are the implications?

4. There is a large potential for microturbines in sawmills ( has this potential been included? It looks like non; this misses important greenhouse gas emission reduction potential

5. Missing important potential in the <10MW industrial category ( back-up systems for large buildings

6. Look at small scale technology; this has been proven in Scandinavia in the forest product sector – this type of technology must be examined for this sector

7. The role of black liquor gasification for Kraft mills is not in the report – this is a highly energetic fuel, with lots of potential for the forestry sector in cogen, and has implications for greenhouse gasses

8. Other technology to look at – coke oven gas in steel mills

9. Look at fuels other than natural gas (the report now only sees one fuel as being a potential, this is a serious drawback)**

10. Look at the technical potential beyond single plant, especially distinct energy (chilling and heating)**

Economic Potential

Lack of analysis of chilling potential and benefits of this; need to build into the economic assumptions

Will see more price volatility in the market, especially summer providing opportunity for absorption chilling

Economic factor in paper industry is age of boilers

Barriers

1. Market place dynamics haven’t begun; this may create opportunities, change the potential for development of cogen

2. Net vs. gross is still an issue

3. Stranded debt

4. Cost of local interconnect – this is a huge issue for small companies especially

5. Back-up rates

6. Economic assumptions neglect positive value of market services in new market

· Grid stability

· Congestion pricing

· Environmental benefits

7. Foreign exchange rate (US) will impact the projects

8. Smaller the plant, the higher the costs

General Comments

1. Report should focus on barriers, potential is more “academic”

2. Class 43.1 rules miss the point that less efficient plants may have greater market & environmental benefits

3. Lack of caps on other sectors is a barrier

4. Uncertainty in emission trading market

5. Labelling of power could be a barrier

6. Need to ensure that certain assets aren’t favoured (i.e. trans over cogen)

2.4
Notes and Next Steps from Workshop

The Workshop was very productive. It allowed the project team to get good feedback from the stakeholder community. The feedback included suggestions of gaps in the analysis, gaps in the information given about assumptions, and some new information.

The next steps can be broken down into a few categories: assumptions, methodology, runs, reporting, and barriers.

Assumptions

Electricity Prices
The Workshop clearly noted the lack of a clear forecast of electricity prices or any rationale for the forecast that was used. In fact, the tables presented to the Workshop used different electricity price forecasts. The tables from AGRA Monenco used the Ministry’s very rough forecast. The tables from Hagler Bailly used a more elaborate forecast, which was close to be not identical to that used by AGRA Monenco. Workshop participants also identified a need to specify generation prices and transmission and distribution tariffs separately.

Several tasks flow from this observation:

· Generate an electricity price forecast and rationale for it.

· The electricity price forecast should identify transmission and distribution rates.

· Communicate the forecast to all team members

· Run the models using the electricity forecast.

Project List for Technical Potential 

The Workshop also noted that the existing list of potential cogeneration projects for the large and medium scale could not really be called a list of technical potential. That list already had significant implicit screening for economic feasibility, since it contained only projects that had actually been considered for implementation. A more complete list would include all locations in the province with a steam boiler. The list of sites also need not be screened for compatibility of steam and electricity load, since the open electricity market can be expected to absorb any excess electricity generation. This discussion led to additional tasks:

· Get the steam boiler inventory prepared for Ontario Hydro in 1988/89, for the Demand/Supply Plan. 

· Look for other inventories of steam boilers. 

Because of the focus on identified projects, the amount of technical potential is seriously underestimated, according to Workshop participants. With new information on boilers, it should be possible to make a new estimate of technical potential.

Interest/Discount Rates and IRR
Several Workshop participants had comments on interest rates and payback periods. These comments were on both sides. Some participants suggested that a 7-year payback period and a 13% IRR are both too stringent. Others thought that a 13% IRR was too high. Given this lack of consensus among participants, there is no need to change the assumptions in the runs. 

Capital Costs
Workshop participants also commented on the capital costs in the tables. One question was whether the capital costs as stated include all the costs of integration of the generation into the grid or distribution system. It is assumed that the costs are for a complete installation. 

For the reciprocating engine technologies, there were comments that the capital costs were too low, as well as comments that the capital costs were about right. 

Actions from this

· Capital costs continue to be inconsistent. AGRA Monenco and Hagler Bailly need to agree on consistent capital cost assumptions, including clarity on whether they include full installation costs or only equipment costs.

Steam Values

One comment noted that the value of steam was too high, at $7.51 per thousand pounds. One participant noted that they can buy steam for as low as $2.45 per thousand pounds. This value is related to the conversion efficiency of the boiler providing the steam.

Most participants said that the assumed efficiency of the steam boiler was too low. For an industrial boiler that is run constantly, 80% efficiency is a minimum, not the 70% assumed in the analysis. A 70% efficiency would be relevant for a boiler that was used in a commercial application, where it was cycled on and off to meet the steam or heat demand.

The action from this comment is to increase the efficiency of the steam boiler being replaced to 80%. 

Methodology

Technical Potential
Some participants questioned whether the calculation of technical potential is relevant. The project should be more about barriers than about calculation of potential. 

Economic Potential

The Workshop was also critical of the methodology for determining economic potential for the large and medium scale. Several participants felt that a simple cutoff based on price did not reflect what actually happens in the market. Others noted that they know of actual installations of a size that would be cut off under the suggested criterion, and they are doing very well. 

Part of the problem in this discussion relates back to the question of whether the economic potential is to be measured against the wholesale market price of electricity or against the delivered price. It is clear that there will be some variance in this rule, depending on the size of the application, but the rule is not clear yet.

The actions from this comment are 

· Make an assumption about the prices (net or gross) which the cogeneration would have to compete against

· Consider the methodology for selecting from the list of potential projects.

Runs
Once the assumptions are compatible, we will need a set of compatible runs of the models. The runs will start from the same set of assumptions.

The runs have to be for more extended time frames. The DISGEN model is already being run for the years up to 2010. Given the proposal, the analysis needs to be extended to 2020. Results for 2015 and 2020 will be sufficient.

The AGRA Monenco model is currently being run only for the immediate year, which is assumed to be 2000. Again, the project needs runs representing the years 2005, and 2010. The data needed for those years are costs and economic potential. 

We also need sensitivities for the runs. At the least, we are committed to running different gas prices. The Workshop noted that the gas price sensitivities should be coordinated with the electricity price ones, so that we are not running very low gas prices with very high electricity prices, for example.

The actions are

· Determine the base case inputs for the cost runs

· Run the costs

· Run DISGEN and the AGRA Monenco models to get economic potential

· Run sensitivities as Reporting

The report needs more detail on the assumptions, especially on the electricity price. 

The report will also need to reflect the additional information. 

The workshop suggested that there could be some use of graphs to present information in the report.

Barriers

The Workshop identified several barriers which are not in the report. The two most clearly identified are more relevant only to smaller generation technologies. These are the requirement that even small boilers have a full time operator, and the possible connection costs for small embedded generation

The action for this item is to verify these barriers and include them in the report. 

3.
LIST OF INVITEES, INVITATION AND AGENDA

3.1
List of Invitees

ABB Alstom Power

Martin Lenzin

(403) 278-7111

Access Capital

Robert McLeese 
(416) 366-4820x225

AMPCO (Association of Major 


Power Consumers of Ontario)
Ken Snelson

(416) 769-8880

ACTO/CU Power

Frank Bajc

(416) 620-1992

BOMA (Building Owners and
Ian Stewart

(416) 862-6005


Manufacturers Association)
Dale Struthers 

(416) 862-6062x8685

Boralax

Yves Rheault

(514) 363-5130

Bowater

Catherine Cobden
(819) 643-7200x7515




Mike Kuriychuk
(807) 475-2432

Canadian Pulp and Paper Assoc.
Lucy Veilleux

(514) 866-6621

Dofasco

Tom McGuire

(905) 544-3761

Henry Wegiel

(905) 548-4037

Susan Olynyk

(905) 548-7200x6107

Enbridge Consumers Gas
Phil Wood

(416) 495-8350

GE Power Systems

Glen Kennedy

(416) 858-5314

John Welch 

(416) 858-5314

Great Lakes Power
Harry Goldgut

(416) 956-5139

Ed Kress 

(416) 956-5140

Green Energy Coalition/Sierra Club
Greg Allen

(416) 488-4425

Hospital for Sick Children
Gregory Dick

(416) 813-5171

IPPSO (Independent Power
Allen Barnstaple
(416) 224-9569

  Producers Society of Ontario)

Jake Brooks

(416) 322-6549

Northland Power

John Brace

(416) 962-6262

Paul Vyrostko

(416) 962-6262

Ontario Clean Air Alliance 
Jack Gibbons

(416) 923-3529

Ontario Forest Industries Association
Craig Gammie

(416) 368-2842

Ontario Lumber Manufacturers
Agnus Rocha

(416) 367-9717

Ontario Power Generation
James Perry

(416)


Pollution Probe

John Welner

(416) 926-1907x236

Pratt & Whitney

Ted Traynor

(905) 564-4135

Probyn & Company

Stephen Probyn
(416) 777-2800x224

Rolls-Royce

Peter Heffernan
(905) 201-0724

Ryerson Polytechnic University
Ian Hamilton

(416) 979-5000x6272

Strathcona Paper

Gerry Murray

(416) 236-4415

Sudbury District Energy Corporation
Brund Pozza 

(705) 673-9133

Toromont Power

Bruce Ander

(416) 667-5724

Toronto Hospital

Mike Horn

(416) 340-3073

Toronto Hydro

Todd Wilcox

(416) 542-2588

TransAlta

Barry Chuddy

(905) 829-7246


Adam White 

(905) 829-7232

TransCanada Energy
 


Finn Greflund

(416) 869-2162

Trigen Canada 

Susan Shaw 

(519) 434-9194x222

Union Gas

Dave Simpson

(519) 436-4651

Aqeel Zaidi 

(519) 496-5221

Craig Lemon

(519) 436-4651

University of Toronto
Harvey Krueger
(416) 978-6650

Westcoast Power
Frank Dixon

(416) 499-3676

3.2
Invitation

(MEST Letterhead)

January 28, 2000

Dear Cogeneration Stakeholder:

I would like to invite you to participate in a half day Stakeholders Workshop on Tuesday February 15 from 9:00 am to 1:30 pm, in the Ottawa Room of the MacDonald Block, 900 Bay Street, Toronto.

The purpose of this Workshop is to seek your comments on a project that we have undertaken to identify the potential for cogeneration applications in Ontario and on the major barriers preventing wider utilization. This project is being undertaken by the Ministry of Energy, Science and Technology in cooperation with the Ministry of Natural Resources and the Ministry of Economic Development and Trade.

The restructuring of the electricity market currently underway in Ontario is expected to remove one of the major barriers to cogeneration projects by allowing access to electricity markets. There are several remaining factors that will be critical in evaluating the likely uptake of cogeneration. 

Many of you participated in a December 9 Workshop where we had preliminary discussions on some of these issues and we thank you for your time and ideas. The consultants on this project (Hagler Bailly, AGRA Monenco Incorporated and Lourie & Love) are currently preparing a draft report on this project, based on the analysis they have undertaken during this project, including the barriers to wider utilization that were discussed at the December 9 Workshop. The draft report will be presented for discussion at the February 15 Workshop. 

Please find attached to this invitation the Agenda for this Workshop and a Confirmation Form. Please fax back the attached Confirmation Form to Peter Love by February 8 or email your confirmation (plove@lourielove.com). If you are unable to attend, another representative from your organization would be welcome. Please indicate if you would like the notes from that December 9 Workshop as well as the draft of the project report emailed to you for your review prior to the February 15 Workshop. It is the Ministry’s intention to distribute the Notes from this Workshop and the Final Report to all participants.

We hope that you will be able to participate at this Workshop and thank you for your time and consideration.

Yours truly,

Doug MacCallum

Team Leader, Energy Economics

Energy Policy Branch

3.3
Agenda

COGENERATION STAKEHOLDERS WORKSHOP

Tuesday February 15, 2000

9:00 – 1:30

Ottawa Room, 2nd floor, MacDonald Block

900 Bay Street (at Wellesley), Toronto

8:30
Registration, Coffee
9:00 
Welcoming Remarks 

9:05
Review of Workshop Objectives and Agenda

9:10
Outline of Objectives of “Potential for Cogeneration in Ontario” Project 

9:15
Review and Discussion of Notes from December 9 Stakeholders Workshop

9:30
Summary of Draft Report “Cogeneration in Ontario”

10:00
Questions/Comments

10:15
Bio Break
10:30
Reconvene into Three Breakout Groups

Each to discuss detailed comments on Draft Report and other related issues

12:00 
Reports from Breakout Groups

12:30
Questions/Comments/Observations

1:00 
Working Lunch/Further Discussions

1:30
Conclusions/Next Steps

� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���








� 	Government of Ontario, “Direction for Change: Charting a Course for Competitive Electricity and Jobs in Ontario,” pg. 10.


� 	Plant sizes in MW are for the electricity output. Heat output is in addition to the electricity.


� 	Natural Resources Canada, Energy Forecasting Division, Energy Policy Branch, Energy Sector, “Canada’s Energy Outlook 1996-2020”, April 1997.


� 	AGRA Monenco, Inc., “Final report: Quantification of Transmission Infrastructure Bypass”, August 1999. Filed with Ontario Energy Board in RP-1999-0044, Exhibit D, Tab S, Schedule 3.


� 	Neill and Gunther (Nova Scotia) Limited, “Opportunities for Increased Cogeneration in the Pulp and Paper Industry”, prepared for Industry Economics and Programs Branch, Canadian Forest Service, NRCan, March 1999.


� 	Ontario Energy Board, “Decision with Reasons”. RP-1999-0044.


� 	Since such operations likely imply a lower capacity factor than for full-time operation, the fixed costs must be spread over fewer operating hours. The LUEC is therefore raised by this operating philosophy.


� 	Natural Resources Canada, Canada’s Energy Outlook, 1996-2020, Appendix D, Table 2, page D-2.


� 	Acres Management Consulting with Diener Consulting, Inc., Replacing Coal-fired Generation with Gas: Financial Costs and Environmental Benefits, Toronto, March 6, 2000. Table B5a, pg. 33.


� 	Sometimes called “default” customers. This refers to customers who do not choose an alternative supplier of commodity electricity.


� 	National Energy Board, Canadian Energy: Supply and Demand to 2025, National Energy Board, 1999.





�PAGE \# "'Page: '#'�'"  ��





[image: image25.wmf]Sector

2000

2005

2010

2015

2020

Offices

1144

1227

1308

1389

1467

Health

857

755

683

617

572

Schools

241

212

192

174

161

Hotels

55

55

56

57

60

Retail

148

144

137

131

134

Other

92

90

85

81

83

Totals

2537

2483

2461

2448

2477

Estimated Technical Cogeneration Potential  

Commercial Sector

Ontario

MW

[image: image26.wmf]Industrial

Commercial

Total

2000

11214

2537

13750

2005

11966

2483

14449

2010

12676

2461

15138

2015

13371

2448

15819

2020

14037

2477

16514

MW



TOTAL COGENERATION

POTENTIAL IN ONTARIO



[image: image27.wmf]Cumulative

Scale

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total

Large/Medium

73

493

634

657

558

210

89

90

94

104

3002

Small

50

55

60

65

72

88

119

122

123

125

879

TOTAL

123

548

694

722

630

298

208

212

217

229

3881

Estimated Economic Cogeneration Installed Annually  

Base Case

MW Installed in Year

[image: image28.wmf]Indicative Performance Attributes of Small Cogeneration Systems

(Estimated Data for 2001) ($ figures in CD$ except where noted)

Assumed

Total

Capacity

Electric-to

Output

Output

Conversion

Total

Total

Size 

Technology

Fuel

Factor

Heat Rate

Heat Rate

Thermal (E/T)

Electricity

Thermal

Efficiency

Heat 

Electricity

(kW)

(%)

(Btu/kWh)

(GJ/kWh)

Ratio

(GJ/h)

(GJ/h)

(%)

(Annual GJ)

(Annual GJ)

75

microturbine

gas

90%

12,186

0.013

0.6

0.27

0.45

75%

3,548

2,129

100

microturbine

gas

90%

11,373

0.012

0.6

0.36

0.60

80%

4,730

2,838

Fuel cells:

200

 Phosphoric Acid

gas

90%

8,530

0.009

1.3

0.72

0.55

71%

4,367

5,676

300

 Solid Oxide-Atmospheric

gas

90%

7,582

0.008

1.5

1.08

0.72

75%

5,676

8,515

600

 Solid Oxide-Atmospheric

gas

90%

7,417

0.008

1.6

2.16

1.35

75%

10,643

17,029

450

 Solid Oxide-Atmos. Hybrid

gas

90%

6,824

0.007

2.0

1.62

0.81

75%

6,386

12,772

900

 Solid Oxide-Atmos. Hybrid

gas

90%

6,824

0.007

2.0

3.24

1.62

75%

12,772

25,544

220

 Solid Oxide-Press. Hybrid

gas

90%

5,687

0.006

4.0

0.79

0.20

75%

1,561

6,244

920

 Solid Oxide-Press. Hybrid

gas

90%

5,687

0.006

4.0

3.31

0.83

75%

6,528

26,112

300

 Molten Carbonate

gas

90%

7,000

0.007

2.0

1.08

0.54

73%

4,257

8,515

1200

 Molten Carbonate

gas

90%

6,700

0.007

2.0

4.32

2.16

76%

17,029

34,059

250

 PEM

gas

90%

8,530

0.009

1.2

0.90

0.75

73%

5,913

7,096

300

Reciprocating engines

gas

90%

9,222

0.010

0.8

1.08

1.35

83%

10,643

8,515

1000

Reciprocating engines

gas

90%

8,124

0.009

1.0

3.60

3.60

84%

28,382

28,382

2500

Reciprocating engines

gas

90%

7,935

0.008

1.1

9.00

8.18

82%

64,505

70,956

5000

Reciprocating engines

diesel

90%

7,417

0.008

1.2

18.00

15.00

84%

118,260

141,912

1500

Aeroderivative turbines

gas

90%

12,186

0.013

0.5

5.40

10.80

84%

85,147

42,574

3000

Aeroderivative turbines

gas

90%

10,339

0.011

0.6

10.80

18.00

88%

141,912

85,147

6000

Aeroderivative turbines

gas

90%

9,749

0.010

0.6

21.60

36.00

93%

283,824

170,294

[image: image29.wmf]Type of Unit

Rated Output

IRR

(MW)

(%)

Cogeneration

Gas Turbine

CCC

250

25.47

SCC

250

43.57

CCC

150

18.62

CCC

100

N/A

CCC

50

N/A

SCC

40

N/A

SCC

26

N/A

SCC

10

N/A

IRR = Internal Rate of Return

IRR computed with electricity rate 

at 50.00 Cdn$/MWh

Returns at $50 per MWh.

Large and Medium Scale

[image: image30.wmf]Cogeneration Potential in Ontario

Estimated Total Costs of Electricity Generated

Base Case Gas Prices

Type of Unit

Rated Output

Fuel

Capital Cost

[1]

Levelized 

Levelized

Plant

Thermal Credit

Availability

Levelized

LUEC without

Levelized 

LUEC with

O&M Cost

Fuel Cost

Heat Rate

[2]

Heat Rate

Tax

[3]

Thermal Credit 

[4]

Thermal Credit

Thermal Credit 

[5]

(MW)

(Cdn$/kW)

(Cdn$/MWh)

(Cdn$/MWh)

(Btu/kWh)

(Btu/kWh)

(Cdn$/MWh)

(Cdn$/MWh)

(Cdn$/MWh)

(Cdn$/MWh)

Cogeneration

[6]

Gas Turbine Plants

CCC 250

Gas

774

4.96

34.73

6,705

< 6,000

93.0%

1.27

50.82

4.21

46.72

SCC 250

Gas

814

4.97

54.41

10,506

4,330

93.0%

1.52

70.62

32.69

38.80

CCC 150

Gas

813

6.25

39.95

7,715

< 6,000

93.0%

1.36

57.80

9.33

48.71

CCC 100

Gas

1,131

9.36

38.94

7,519

< 6,000

93.0%

2.10

64.88

8.65

56.46

CCC 50

Gas

1,626

18.61

37.61

7,262

< 6,000

93.0%

3.25

80.55

6.98

73.76

SCC 40

Gas

1,290

17.29

44.81

8,652

4,350

93.0%

2.65

81.00

24.78

56.88

SCC 26

Gas

1,563

20.37

56.01

10,815

4,840

93.0%

3.29

99.23

36.40

63.80

SCC 10

Gas

1,600

22.50

62.50

11,124

4,780

93.0%

4.37

116.05

39.35

78.50

Note:

[1]

 Excludes Interest during Construction 

[2] 

Include 3% Degradation.

[3] 

Tax cost includes Income Tax only. Capital taxes, GST and municipal taxes are not included.

[4] 

LUEC is based on the sales value of steam equal to zero Cdn$/klb

[5] 

LUEC is based on the sale value of steam equal to 7.51 Cdn$/klb

[6] 

Thermal recovery of CCC plants is designed to just meet the Class 43 heat rate of 6000 Btu/kWh.

Legend:

CCC250 - 250MW Combined Cycle Cogeneration*

SCC250 - 250MW Simple Cycle Cogeneration*

CCC150 - 150MW Combined Cycle Cogeneration*

SCC40   - 40MW Simple Cycle Cogeneration*

CCC100 - 100MW Combined Cycle Cogeneration*

SCC26   - 26MW Simple Cycle Cogeneration*

CCC50   - 50 MW Combined Cycle Cogeneration*

SCC10   - 10MW Simple Cycle Cogeneration*

* Class 43.1 eligible

[image: image31.wmf]Indicative Cost Attributes of Small Cogeneration Systems

(Estimated Data for 2001) ($ figures in CD$ except where noted)

Installed

Capital 

O&M 

Fuel

Thermal

Adjusted

Size 

Technology

Fuel

Cost

Cost

Cost

Heat Rate

Availability

Taxes

LUEC

Credit

LUEC

(kW)

($/kW) (1)

($/MWh) (2)

($/MWh)

(Btu/kWh)

(%)

 ($/MWh)

 ($/MWh)(3)

 ($/MWh)

75

Microturbine

gas

1575

18.42

68.55

12,186

92%

115.51

37.64

77.87

100

Microturbine

gas

1350

15.04

63.97

11,373

92%

103.48

37.64

65.84

Fuel cells:

200

 Phosphoric Acid

gas

3000

17.64

47.98

8,530

98%

119.98

17.37

102.61

300

 Solid Oxide-Atmospheric

gas

3150

8.94

42.65

7,582

96%

108.67

15.05

93.61

600

 Solid Oxide-Atmospheric

gas

2850

5.84

41.72

7,417

95%

99.20

14.11

85.09

450

 Solid Oxide-Atmos. Hybrid

gas

2400

13.43

38.39

6,824

93%

95.30

11.29

84.01

900

 Solid Oxide-Atmos. Hybrid

gas

2250

13.43

38.39

6,824

93%

92.59

11.29

81.30

220

 Solid Oxide-Press. Hybrid

gas

2700

17.17

31.99

5,687

92%

98.08

5.65

92.44

920

 Solid Oxide-Press. Hybrid

gas

2250

8.31

31.99

5,687

92%

81.06

5.65

75.42

300

 Molten Carbonate

gas

3000

18.39

39.38

7,000

92%

112.12

11.29

100.83

1200

 Molten Carbonate

gas

2850

13.34

37.69

6,700

92%

102.67

11.29

91.38

250

 PEM

gas

3000

13.61

47.98

8,530

93%

115.95

18.82

97.13

300

Reciprocating engines

gas

1650

23.89

51.87

9,222

92%

105.66

28.23

77.43

1000

Reciprocating engines

gas

1463

14.86

45.70

8,124

92%

87.06

22.58

64.48

2500

Reciprocating engines

gas

1350

11.25

44.63

7,935

92%

80.34

20.53

59.81

5000

Reciprocating engines

diesel

900

20.08

66.75

7,417

95%

103.14

30.11

73.03

1500

Aeroderivative turbines

gas

2200

10.57

68.55

12,186

92%

118.98

45.16

73.81

3000

Aeroderivative turbines

gas

1900

8.05

58.16

10,339

92%

100.64

37.64

63.00

6000

Aeroderivative turbines

gas

1850

7.50

54.838

9,749

92%

95.854

37.64

58.22

(1) Including gas compression

Assumptions

    and moderate emission controls

Capacity Factor

90%

(2) With fixed O&M converted

Gas Price

5.625

$/MMBtu

Diesel Price

9

$/MMBtu

     at assumed capacity factor

5.33

$/GJ

8.53

$/GJ

(3) Most small cogen systems

Boiler Efficiency

85%

Capital Recovery

7

years

     limited to lower temperature

     applications -- exception small gas turbines

Exchange Rate Conversion

1.5

CD$/US$

[image: image32.wmf]Cost

($/MWh)

Type

Size

2000

2005

2010

(kW)

Microturbine

100

65.84

55.04

51.02

Solid Oxide-Atmospheric fuel cell

600

85.09

72.36

67.97

Solid Oxide-Press. Hybrid fuel cell

920

75.42

67.68

60.15

Reciprocating engines

300

77.43

74.18

69.34

Reciprocating engines

2500

59.81

57.01

52.58

Aeroderivative turbines

1500

73.81

66.50

59.37

Aeroderivative turbines

3000

63.00

56.03

49.34

Aeroderivative turbines

6000

58.22

49.49

46.41



Small

Cogeneration Technologies

LUEC Cost Forecast

[image: image33.wmf]HIGH CASE (Low gas prices)

Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Total

Large/Medium

90

458

639

679

869

452

304

156

161

173

3982

Small

65

72

78

85

100

133

132

137

158

177

1136

TOTAL 

155

529

717

763

969

585

436

293

319

350

5118

LOW CASE High gas prices)

Large/Medium

47

239

330

345

439

215

137

59

62

71

1944

Small

34

37

40

44

48

51

65

75

90

105

588

TOTAL

81

276

370

388

487

266

202

134

152

176

2532

Estimated Economic Cogeneration Installed Annually  

High and Low Cases

MW Installed in Year

[image: image34.wmf]MW

TWh.

2000

11214

28.43

2005

11966

31.06

2010

12676

33.09

2015

13371

34.96

2020

14037

36.44



POTENTIAL IN ONTARIO

Analytical Method

INDUSTRIAL COGENERATION

[image: image35.wmf]Fraction of

Electricity

Sector

Electricity

Heat

in Large

PJ

PJ

Electricity

Heat

Electricity

Heat

Buildings

Offices

46.34

52.44

4.35%

1.14%

2.60%

1.07%

46%

Health

9.78

41.79

0.28%

-2.50%

0.11%

-1.87%

40%

Schools

9.31

34.91

0.36%

-2.64%

0.37%

-2.00%

27%

Hotels

14.82

12.04

1.50%

0.65%

0.33%

0.43%

10%

Retail

55.05

33.16

1.74%

-0.89%

0.43%

-0.50%

10%

Other

20.26

35.29

1.99%

-1.35%

1.09%

-0.50%

5%

Data Source:  Office of Energy Efficiency, NRCan

Energy Use 1997

Growth Rate

Growth Rate

Data for Estimation of Technical Cogeneration Potential  

Commercial Sector

Ontario

Historical Data 

Assumptions

1981-97

2000-20

Average Annual

Average Annual

[image: image36.wmf]Cumulative

2001

2002

2003

2004

2005

2006

2007

2008

2009

2010

Totals

Emissions from Cogeneration 

Large Applications

0.2

1.7

3.6

5.6

7.3

8.7

9.0

9.3

9.6

10.0

65.1

Small Applications

0.1

0.3

0.5

0.8

1.2

1.6

2.0

2.5

2.9

3.4

15.3

TOTAL EMISSIONS 

0.3

2.0

4.1

6.4

8.5

10.3

11.0

11.8

12.6

13.4

80.3

Avoided Emissions

Electricity Generation

0.8

5.1

10.6

16.5

21.8

24.3

25.9

27.6

29.3

31.2

193.1

Heat Production

0.2

0.8

1.6

2.5

3.3

4.7

5.3

5.8

5.5

6.0

35.6

TOTAL AVOIDED

1.0

5.9

12.2

19.0

25.1

29.0

31.2

33.4

34.8

37.2

228.8

NET EMISSION REDUCTION

0.6

3.9

8.1

12.6

16.7

18.7

20.2

21.6

22.2

23.8

148.4

Mtons CO2

GHG EMISSION SAVINGS FROM COGENERATION 

BASE CASE

[image: image37.wmf]5 yr 

5 yr 

5 yr 

YEAR

$

AAGR

$

AAGR

$

AAGR

2000

3.00

3.00

3.00

2001

2.90

3.03

3.09

2002

2.79

3.06

3.19

2003

2.70

3.09

3.29

2004

2.60

3.12

3.39

2005

2.51

-3.50%

3.15

1.00%

3.49

3.10%

2006

2.42

3.21

3.60

2007

2.34

3.26

3.71

2008

2.26

3.32

3.83

2009

2.18

3.37

3.95

2010

2.10

-3.50%

3.43

1.70%

4.07

3.10%

2011

2.15

3.51

4.18

2012

2.19

3.60

4.29

2013

2.24

3.68

4.41

2014

2.29

3.77

4.53

2015

2.34

2.20%

3.86

2.40%

4.65

2.70%

2016

2.39

3.95

4.78

2017

2.45

4.05

4.91

2018

2.50

4.15

5.04

2019

2.56

4.25

5.17

2020

2.61

2.20%

4.35

2.40%

5.31

2.70%

BASE CASE

HIGH CASE

LOW CASE

Alberta Border

FORECAST GAS PRICES

(All prices in $2000/Mcf)

[image: image38.wmf]Transmission

YEAR

Tolls 

Sudbury

Toronto

Sudbury

Toronto

Sudbury

Toronto

2000

0.98

0.40

0.40

0.80

0.80

2.50

2.75

2001

0.97

0.40

0.40

0.80

0.80

2.44

2.69

2002

0.95

0.40

0.40

0.80

0.80

2.39

2.63

2003

0.94

0.40

0.40

0.80

0.80

2.34

2.57

2004

0.93

0.40

0.40

0.80

0.80

2.29

2.52

2005

0.91

0.40

0.40

0.80

0.80

2.24

2.46

2006

0.90

0.40

0.40

0.80

0.80

2.19

2.41

2007

0.89

0.40

0.40

0.80

0.80

2.14

2.35

2008

0.87

0.40

0.40

0.80

0.80

2.09

2.30

2009

0.86

0.40

0.40

0.80

0.80

2.05

2.25

2010

0.85

0.40

0.40

0.80

0.80

2.00

2.20

2011

0.84

0.40

0.40

0.80

0.80

1.97

2.17

2012

0.83

0.40

0.40

0.80

0.80

1.94

2.13

2013

0.82

0.40

0.40

0.80

0.80

1.91

2.10

2014

0.82

0.40

0.40

0.80

0.80

1.88

2.07

2015

0.81

0.40

0.40

0.80

0.80

1.85

2.04

2016

0.80

0.40

0.40

0.80

0.80

1.83

2.01

2017

0.79

0.40

0.40

0.80

0.80

1.80

1.98

2018

0.78

0.40

0.40

0.80

0.80

1.77

1.95

2019

0.78

0.40

0.40

0.80

0.80

1.75

1.92

2020

0.77

0.40

0.40

0.80

0.80

1.72

1.89

Distribution Tariffs for Cogeneration

DISTRIBUTION AND TRANSMISSION CHARGES

(All prices in $2000/Mcf)

>50 MW

10 MW

<500 kW

[image: image39.wmf]Sudbury

Toronto

YEAR

Low

Base

High

Low

Base

High

Low

Base

High

Low

Base

High

2000

4.38

4.38

4.38

4.78

4.78

4.78

6.48

6.48

6.48

6.73

6.73

6.73

2001

4.26

4.40

4.46

4.66

4.80

4.86

6.31

6.44

6.50

6.55

6.69

6.75

2002

4.15

4.41

4.54

4.55

4.81

4.94

6.14

6.40

6.53

6.38

6.64

6.77

2003

4.03

4.43

4.63

4.43

4.83

5.03

5.97

6.37

6.56

6.21

6.60

6.80

2004

3.93

4.45

4.72

4.33

4.85

5.12

5.81

6.33

6.60

6.04

6.56

6.83

2005

3.82

4.47

4.81

4.22

4.87

5.21

5.66

6.30

6.64

5.88

6.53

6.87

2006

3.72

4.51

4.90

4.12

4.91

5.30

5.51

6.29

6.69

5.73

6.51

6.91

2007

3.62

4.55

5.00

4.02

4.95

5.40

5.36

6.29

6.74

5.58

6.50

6.95

2008

3.53

4.59

5.10

3.93

4.99

5.50

5.22

6.28

6.80

5.43

6.49

7.00

2009

3.44

4.64

5.21

3.84

5.04

5.61

5.08

6.28

6.86

5.29

6.48

7.06

2010

3.35

4.68

5.32

3.75

5.08

5.72

4.95

6.28

6.92

5.15

6.48

7.12

2011

3.39

4.75

5.42

3.79

5.15

5.82

4.96

6.32

6.99

5.16

6.52

7.19

2012

3.43

4.83

5.53

3.83

5.23

5.93

4.97

6.37

7.07

5.16

6.56

7.26

2013

3.47

4.91

5.63

3.87

5.31

6.03

4.98

6.42

7.15

5.17

6.61

7.34

2014

3.51

4.99

5.75

3.91

5.39

6.15

4.99

6.47

7.23

5.18

6.66

7.42

2015

3.55

5.07

5.86

3.95

5.47

6.26

5.01

6.52

7.31

5.19

6.71

7.50

2016

3.59

5.16

5.98

3.99

5.56

6.38

5.02

6.58

7.40

5.20

6.76

7.59

2017

3.64

5.24

6.10

4.04

5.64

6.50

5.04

6.64

7.50

5.22

6.82

7.68

2018

3.68

5.33

6.22

4.08

5.73

6.62

5.06

6.70

7.59

5.23

6.88

7.77

2019

3.73

5.42

6.35

4.13

5.82

6.75

5.08

6.77

7.70

5.25

6.94

7.87

2020

3.78

5.52

6.48

4.18

5.92

6.88

5.10

6.84

7.80

5.27

7.01

7.97

10 MW

<500 kW

DELIVERED PRICES FOR GAS FOR COGENERATION

(All prices in $2000/Mcf)

LOW, BASE AND HIGH CASES

>50 MW

_1022676204.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls						Capacity Factor						90%

		(2) With fixed O&M converted						Gas Price						5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems						Boiler Efficiency						85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines								Exchange Rate Conversion						1.5		CD$/US$





tab26

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300

				Reciprocating engines		2500

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(MW)

				CCC		250		47.24

				SCC		250		42.78

				CCC		100		57.52

				CCC		50		74.61

				SCC		10		72.99





tab32_5

		

												Table 3-5

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		1472		12685

				2005		11966		31.06				2005		11966		1610		13577

				2010		12676		33.09				2010		12676		1773		14449

				2015		13371		34.96				2015		13371		1960		15331

				2020		14037		36.44				2020		14037		2171		16208





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"






_1028447558.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

								Cost

				Type		Size				($/MWh)

						(MW)		2000		2005		2010

				CCC		250		47.24		45.79		44.34

				CCC		50		74.61		73.06		71.51





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls				Capacity Factor								90%

		(2) With fixed O&M converted				Gas Price								5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems				Boiler Efficiency								85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines

						Exchange Rate Conversion										1.5		CD$/US$





tab25

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300		77.43		74.18		69.34

				Reciprocating engines		2500		59.81		57.01		52.58

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





lgcalc

		

								MW

		Small				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

		Large

		AGRA Monenco est				2328

		Plus 5%				2444.4		122.22		488.88		611.1		611.1		488.88		122.22										2444.4

		yearly shares						0.05		0.2		0.25		0.25		0.2		0.05										1

		Total potential				11214		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676

		Analytical estimate

		Potential % total				0.2179851087		0.225		0.23		0.235		0.24		0.25		0.26		0.27		0.28		0.29		0.3

		Penetration curve						5		8		15		15		11		10		9		8		8		8		97

		cogeneration installed						128		212		411		425		329		315		298		278		291		304		2990.4633105548

		Market timing - small : from Steve Williams

		%accessible						0.016		0.0301		0.046		0.0588		0.0572		0.055		0.0522		0.0464		0.0464		0.0464

		%exposed						4		7		10		12		11		10		9		8		8		8		87

		%targetable						40		43		46		49		52		55		58		58		58		58

		Market timing - large

		%accessible						2.5%		4.1%		6.2%		8.3%		6.3%		5.4%		5.0%		5.1%		5.3%		5.4%

		%exposed						5		8		12		15		11		9		8		8		8		8		92

		%targetable						50		51		52		55		57		60		62		64		66		68

		%success						0.4		0.4		0.4		0.45		0.45		0.45		0.5		0.5		0.5		0.55

								113.6416843299		187.9203420968		291.1655199732		438.6631961191		337.6320346218		294.2323132615		303.8061806452		317.239623437		330.9001439422		379.2665163771		2994.4675548038

																																				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL								2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895

		AGRA Monenco pot				2328																										AGRA Monenco pot				2858																										AGRA Monenco pot				1500

		plus 5%				2444.4																										plus 5%				3000.9																										plus 5%				1575

		Potential % total				0.2179851087		0.2179851087		0.2229851087		0.2279851087		0.2329851087		0.2379851087		0.2429851087		0.2479851087		0.2529851087		0.2629851087		0.2729851087						Potential % total				0.2676123027		0.2676123027		0.2776123027		0.2876123027		0.2976123027		0.3076123027		0.3176123027		0.3276123027		0.3376123027		0.3526123027		0.3676123027						Potential % total				0.1404543226		0.1404543226		0.1437543226		0.1470543226		0.1503543226		0.1536543226		0.1569543226		0.1602543226		0.1635543226		0.1710543226		0.1785543226

		Potential						2477.2194916315		2567.6126174837		2659.5113274477		2752.9156215234		2847.8254997109		2942.1428244176		3037.8793848338		3135.0351809594		3296.2806946017		3460.3646796628		3002.1926028449				Potential						3041.1912831111		3196.6298346639		3355.0795544401		3516.5404424397		3681.0124986628		3845.75319162		4013.3323559959		4183.7499917907		4419.6765808115		4659.8608769606		3982.1577229956				Potential						1596.1465796594		1655.2917579046		1715.4306216635		1776.5631709362		1838.6894057226		1900.4540505232		1963.155390892		2026.7934268291		2144.0113630524		2263.3581528399		1943.5699875476

		Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99

		cogeneration installed - one curve						99		154		532		358		285		441		304		251		231		208		2861.9830889976				cogeneration installed - one curve						122		192		671		457		368		577		401		335		309		280		3711.578086636				cogeneration installed - one curve						64		99		343		231		184		285		196		162		150		136		1850.4810511854

		diff								90.3931258523		91.898709964		93.4042940757		94.9098781874		94.3173247068		95.7365604162		97.1557961256		161.2455136423		164.0839850611		983.1451880314				diff								155.4385515528		158.4497197762		161.4608879997		164.4720562231		164.7406929571		167.5791643759		170.4176357948		235.9265890208		240.1842961491		1618.6695938495				diff								59.1451782452		60.1388637589		61.1325492727		62.1262347864		61.7646448006		62.7013403688		63.638035937		117.2179362233		119.3467897875		667.2115731804

								2444.4																				2444.4										3000.9																				3000.9										1575																				1575

		Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100

		Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100

		Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100

		Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100

		Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100

		Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90

		Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70

		Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45

		Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20

		Penetration curve 10																								5						Penetration curve 10																								5						Penetration curve 10																								5

		Install 1				48.888		73.332		366.66		488.88		488.88		611.1		244.44		122.22								2444.4				Install 1				60.018		90.027		450.135		600.18		600.18		750.225		300.09		150.045								3000.9				Install 1				31.5		47.25		236.25		315		315		393.75		157.5		78.75								1575

		Install 2								4.5196562926		18.0786251705		22.5982814631		22.5982814631		18.0786251705		4.5196562926								90.3931258523				Install 2								7.7719275776		31.0877103106		38.8596378882		38.8596378882		31.0877103106		7.7719275776								155.4385515528				Install 2								2.9572589123		11.829035649		14.7862945613		14.7862945613		11.829035649		2.9572589123								59.1451782452

		Install 3										4.5949354982		18.3797419928		22.974677491		22.974677491		18.3797419928		4.5949354982						91.898709964				Install 3										7.9224859888		31.6899439552		39.6124299441		39.6124299441		31.6899439552		7.9224859888						158.4497197762				Install 3										3.0069431879		12.0277727518		15.0347159397		15.0347159397		12.0277727518		3.0069431879						60.1388637589

		Install 4												4.6702147038		18.6808588151		23.3510735189		23.3510735189		18.6808588151		4.6702147038				93.4042940757				Install 4												8.0730444		32.2921775999		40.3652219999		40.3652219999		32.2921775999		8.0730444				161.4608879997				Install 4												3.0566274636		12.2265098545		15.2831373182		15.2831373182		12.2265098545		3.0566274636				61.1325492727

		Install 5														4.7454939094		18.9819756375		23.7274695469		23.7274695469		18.9819756375		4.7454939094		94.9098781874				Install 5														8.2236028112		32.8944112446		41.1180140558		41.1180140558		32.8944112446		8.2236028112		164.4720562231				Install 5														3.1063117393		12.4252469573		15.5315586966		15.5315586966		12.4252469573		3.1063117393		62.1262347864

		Install 6																4.7158662353		14.147598706		23.5793311767		23.5793311767		18.8634649414		84.8855922361				Install 6																8.2370346479		24.7111039436		41.1851732393		41.1851732393		32.9481385914		148.2666236614				Install 6																3.08823224		9.2646967201		15.4411612002		15.4411612002		12.3529289601		55.5881803206

		Install 7																		4.7868280208		14.3604840624		23.934140104		23.934140104		67.0155922913				Install 7																		8.3789582188		25.1368746564		41.894791094		41.894791094		117.3054150632				Install 7																		3.1350670184		9.4052010553		15.6753350922		15.6753350922		43.8909382582

		Install 8																				4.8577898063		14.5733694188		24.2889490314		43.7201082565				Install 8																				8.5208817897		25.5626453692		42.6044089487		76.6879361076				Install 8																				3.1819017969		9.5457053906		15.9095089843		28.6371161717

		Install 9																						8.0622756821		24.1868270463		32.2491027285				Install 9																						11.796329451		35.3889883531		47.1853178042				Install 9																						5.8608968112		17.5826904335		23.4435872447

		Install 10																								8.2041992531		8.2041992531				Install 10																								12.0092148075		12.0092148075				Install 10																								5.9673394894		5.9673394894

						48.888		73.332		371.1796562926		511.5535606687		534.5282381597		680.0993116786		332.5422180532		211.132368078		89.8008689056		93.801306723		104.2230742856		3002.1926028449								60.018		90.027		457.9069275776		639.1901962994		678.8026262434		869.2128482433		452.286808147		304.0801697509		156.1756073299		161.4063947981		173.0691446058		3982.1577229956								31.5		47.25		239.2072589123		329.835978837		344.8706947767		438.9038320949		215.1603681042		136.9494914173		58.7932757914		62.004972915		70.5941146988		1943.5699875476





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		85%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																above (cols. N,O): total MW if elec limited, with 250 MW or 18 MW units																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"





tab44

		

						Estimated Economic Cogeneration Installed Annually

						Large and Medium Scale Applications

						Base Case

								MW Installed in Year

																														Cumulative

										2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential				73		493		634		657		558		210		89		90		94		104		3002





tab 47

		

						Estimated Economic Cogeneration Installed Annually

						High and Low Cases

								MW Installed in Year

						HIGH CASE (Low gas prices)																						Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		90		458		639		679		869		452		304		156		161		173		3982

						Small		65		71.5		78		84.5		100		133		132		137		158		177		1136

						TOTAL		155		529		717		763		969		585		436		293		319		350		5118

						LOW CASE High gas prices)

						Large/Medium		47		239		330		345		439		215		137		59		62		71		1944

						Small		34		37		40		44		48		51		65		75		90		105		588

						TOTAL		81		276		370		388		487		266		202		134		152		176		2532





tab46

		

						Estimated Economic Cogeneration Installed Annually

						Base Case

								MW Installed in Year

																												Cumulative

						Scale		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		73		493		634		657		558		210		89		90		94		104		3002

						Small		50		55		60		65		72		88		119		122		123		125		879

						TOTAL		123		548		694		722		630		298		208		212		217		229		3881





tab45

								MW

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

						Estimated Economic Cogeneration Installed Annually

						Small Scale Applications

						Base Case

								MW Installed in Year

																												Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential		50		55		60		65		72		88		119		122		123		125		879





tab42

		

				Economic Potential

				Large and Medium Scale

				Returns at $50 per MWh.

				Type of Unit				Rated Output				IRR

								(MW)				(%)

				Cogeneration

						Gas Turbine		CCC		250		25.47

								SCC		250		43.57

								CCC		150		18.62

								CCC		100		N/A

								CCC		50		N/A

								SCC		40		N/A

								SCC		26		N/A

								SCC		10		N/A

				IRR = Internal Rate of Return

				IRR computed with electricity rate

						at 50.00 Cdn$/MWh





tab32_5

		

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		2537		13750

				2005		11966		31.06				2005		11966		2483		14449

				2010		12676		33.09				2010		12676		2461		15138

				2015		13371		34.96				2015		13371		2448		15819

				2020		14037		36.44				2020		14037		2477		16514





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible






_1028449190.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

								Cost

				Type		Size				($/MWh)

						(MW)		2000		2005		2010

				CCC		250		47.24		45.79		44.34

				CCC		50		74.61		73.06		71.51





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls				Capacity Factor								90%

		(2) With fixed O&M converted				Gas Price								5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems				Boiler Efficiency								85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines

						Exchange Rate Conversion										1.5		CD$/US$





tab25

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300		77.43		74.18		69.34

				Reciprocating engines		2500		59.81		57.01		52.58

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





lgcalc

		

								MW

		Small				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

		Large

		AGRA Monenco est				2328

		Plus 5%				2444.4		122.22		488.88		611.1		611.1		488.88		122.22										2444.4

		yearly shares						0.05		0.2		0.25		0.25		0.2		0.05										1

		Total potential				11214		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676

		Analytical estimate

		Potential % total				0.2179851087		0.225		0.23		0.235		0.24		0.25		0.26		0.27		0.28		0.29		0.3

		Penetration curve						5		8		15		15		11		10		9		8		8		8		97

		cogeneration installed						128		212		411		425		329		315		298		278		291		304		2990.4633105548

		Market timing - small : from Steve Williams

		%accessible						0.016		0.0301		0.046		0.0588		0.0572		0.055		0.0522		0.0464		0.0464		0.0464

		%exposed						4		7		10		12		11		10		9		8		8		8		87

		%targetable						40		43		46		49		52		55		58		58		58		58

		Market timing - large

		%accessible						2.5%		4.1%		6.2%		8.3%		6.3%		5.4%		5.0%		5.1%		5.3%		5.4%

		%exposed						5		8		12		15		11		9		8		8		8		8		92

		%targetable						50		51		52		55		57		60		62		64		66		68

		%success						0.4		0.4		0.4		0.45		0.45		0.45		0.5		0.5		0.5		0.55

								113.6416843299		187.9203420968		291.1655199732		438.6631961191		337.6320346218		294.2323132615		303.8061806452		317.239623437		330.9001439422		379.2665163771		2994.4675548038

																																				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL								2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895

		AGRA Monenco pot				2328																										AGRA Monenco pot				2858																										AGRA Monenco pot				1500

		plus 5%				2444.4																										plus 5%				3000.9																										plus 5%				1575

		Potential % total				0.2179851087		0.2179851087		0.2229851087		0.2279851087		0.2329851087		0.2379851087		0.2429851087		0.2479851087		0.2529851087		0.2629851087		0.2729851087						Potential % total				0.2676123027		0.2676123027		0.2776123027		0.2876123027		0.2976123027		0.3076123027		0.3176123027		0.3276123027		0.3376123027		0.3526123027		0.3676123027						Potential % total				0.1404543226		0.1404543226		0.1437543226		0.1470543226		0.1503543226		0.1536543226		0.1569543226		0.1602543226		0.1635543226		0.1710543226		0.1785543226

		Potential						2477.2194916315		2567.6126174837		2659.5113274477		2752.9156215234		2847.8254997109		2942.1428244176		3037.8793848338		3135.0351809594		3296.2806946017		3460.3646796628		3002.1926028449				Potential						3041.1912831111		3196.6298346639		3355.0795544401		3516.5404424397		3681.0124986628		3845.75319162		4013.3323559959		4183.7499917907		4419.6765808115		4659.8608769606		3982.1577229956				Potential						1596.1465796594		1655.2917579046		1715.4306216635		1776.5631709362		1838.6894057226		1900.4540505232		1963.155390892		2026.7934268291		2144.0113630524		2263.3581528399		1943.5699875476

		Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99

		cogeneration installed - one curve						99		154		532		358		285		441		304		251		231		208		2861.9830889976				cogeneration installed - one curve						122		192		671		457		368		577		401		335		309		280		3711.578086636				cogeneration installed - one curve						64		99		343		231		184		285		196		162		150		136		1850.4810511854

		diff								90.3931258523		91.898709964		93.4042940757		94.9098781874		94.3173247068		95.7365604162		97.1557961256		161.2455136423		164.0839850611		983.1451880314				diff								155.4385515528		158.4497197762		161.4608879997		164.4720562231		164.7406929571		167.5791643759		170.4176357948		235.9265890208		240.1842961491		1618.6695938495				diff								59.1451782452		60.1388637589		61.1325492727		62.1262347864		61.7646448006		62.7013403688		63.638035937		117.2179362233		119.3467897875		667.2115731804

								2444.4																				2444.4										3000.9																				3000.9										1575																				1575

		Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100

		Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100

		Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100

		Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100

		Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100

		Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90

		Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70

		Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45

		Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20

		Penetration curve 10																								5						Penetration curve 10																								5						Penetration curve 10																								5

		Install 1				48.888		73.332		366.66		488.88		488.88		611.1		244.44		122.22								2444.4				Install 1				60.018		90.027		450.135		600.18		600.18		750.225		300.09		150.045								3000.9				Install 1				31.5		47.25		236.25		315		315		393.75		157.5		78.75								1575

		Install 2								4.5196562926		18.0786251705		22.5982814631		22.5982814631		18.0786251705		4.5196562926								90.3931258523				Install 2								7.7719275776		31.0877103106		38.8596378882		38.8596378882		31.0877103106		7.7719275776								155.4385515528				Install 2								2.9572589123		11.829035649		14.7862945613		14.7862945613		11.829035649		2.9572589123								59.1451782452

		Install 3										4.5949354982		18.3797419928		22.974677491		22.974677491		18.3797419928		4.5949354982						91.898709964				Install 3										7.9224859888		31.6899439552		39.6124299441		39.6124299441		31.6899439552		7.9224859888						158.4497197762				Install 3										3.0069431879		12.0277727518		15.0347159397		15.0347159397		12.0277727518		3.0069431879						60.1388637589

		Install 4												4.6702147038		18.6808588151		23.3510735189		23.3510735189		18.6808588151		4.6702147038				93.4042940757				Install 4												8.0730444		32.2921775999		40.3652219999		40.3652219999		32.2921775999		8.0730444				161.4608879997				Install 4												3.0566274636		12.2265098545		15.2831373182		15.2831373182		12.2265098545		3.0566274636				61.1325492727

		Install 5														4.7454939094		18.9819756375		23.7274695469		23.7274695469		18.9819756375		4.7454939094		94.9098781874				Install 5														8.2236028112		32.8944112446		41.1180140558		41.1180140558		32.8944112446		8.2236028112		164.4720562231				Install 5														3.1063117393		12.4252469573		15.5315586966		15.5315586966		12.4252469573		3.1063117393		62.1262347864

		Install 6																4.7158662353		14.147598706		23.5793311767		23.5793311767		18.8634649414		84.8855922361				Install 6																8.2370346479		24.7111039436		41.1851732393		41.1851732393		32.9481385914		148.2666236614				Install 6																3.08823224		9.2646967201		15.4411612002		15.4411612002		12.3529289601		55.5881803206

		Install 7																		4.7868280208		14.3604840624		23.934140104		23.934140104		67.0155922913				Install 7																		8.3789582188		25.1368746564		41.894791094		41.894791094		117.3054150632				Install 7																		3.1350670184		9.4052010553		15.6753350922		15.6753350922		43.8909382582

		Install 8																				4.8577898063		14.5733694188		24.2889490314		43.7201082565				Install 8																				8.5208817897		25.5626453692		42.6044089487		76.6879361076				Install 8																				3.1819017969		9.5457053906		15.9095089843		28.6371161717

		Install 9																						8.0622756821		24.1868270463		32.2491027285				Install 9																						11.796329451		35.3889883531		47.1853178042				Install 9																						5.8608968112		17.5826904335		23.4435872447

		Install 10																								8.2041992531		8.2041992531				Install 10																								12.0092148075		12.0092148075				Install 10																								5.9673394894		5.9673394894

						48.888		73.332		371.1796562926		511.5535606687		534.5282381597		680.0993116786		332.5422180532		211.132368078		89.8008689056		93.801306723		104.2230742856		3002.1926028449								60.018		90.027		457.9069275776		639.1901962994		678.8026262434		869.2128482433		452.286808147		304.0801697509		156.1756073299		161.4063947981		173.0691446058		3982.1577229956								31.5		47.25		239.2072589123		329.835978837		344.8706947767		438.9038320949		215.1603681042		136.9494914173		58.7932757914		62.004972915		70.5941146988		1943.5699875476





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		85%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																above (cols. N,O): total MW if elec limited, with 250 MW or 18 MW units																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"





tab44

		

						Estimated Economic Cogeneration Installed Annually

						Large and Medium Scale Applications

						Base Case

								MW Installed in Year

																														Cumulative

										2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential				73		493		634		657		558		210		89		90		94		104		3002





tab 47

		

						Estimated Economic Cogeneration Installed Annually

						High and Low Cases

								MW Installed in Year

						HIGH CASE (Low gas prices)																						Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		90		458		639		679		869		452		304		156		161		173		3982

						Small		65		72		78		85		100		133		132		137		158		177		1136

						TOTAL		155		529		717		763		969		585		436		293		319		350		5118

						LOW CASE High gas prices)

						Large/Medium		47		239		330		345		439		215		137		59		62		71		1944

						Small		34		37		40		44		48		51		65		75		90		105		588

						TOTAL		81		276		370		388		487		266		202		134		152		176		2532





tab46

		

						Estimated Economic Cogeneration Installed Annually

						Base Case

								MW Installed in Year

																												Cumulative

						Scale		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		73		493		634		657		558		210		89		90		94		104		3002

						Small		50		55		60		65		72		88		119		122		123		125		879

						TOTAL		123		548		694		722		630		298		208		212		217		229		3881





tab45

								MW

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

						Estimated Economic Cogeneration Installed Annually

						Small Scale Applications

						Base Case

								MW Installed in Year

																												Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential		50		55		60		65		72		88		119		122		123		125		879





tab42

		

				Economic Potential

				Large and Medium Scale

				Returns at $50 per MWh.

				Type of Unit				Rated Output				IRR

								(MW)				(%)

				Cogeneration

						Gas Turbine		CCC		250		25.47

								SCC		250		43.57

								CCC		150		18.62

								CCC		100		N/A

								CCC		50		N/A

								SCC		40		N/A

								SCC		26		N/A

								SCC		10		N/A

				IRR = Internal Rate of Return

				IRR computed with electricity rate

						at 50.00 Cdn$/MWh





tab32_5

		

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		2537		13750

				2005		11966		31.06				2005		11966		2483		14449

				2010		12676		33.09				2010		12676		2461		15138

				2015		13371		34.96				2015		13371		2448		15819

				2020		14037		36.44				2020		14037		2477		16514





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible






_1028459015.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

								Cost

				Type		Size				($/MWh)

						(MW)		2000		2005		2010

				CCC		250		47.24		45.79		44.34

				CCC		50		74.61		73.06		71.51





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls				Capacity Factor								90%

		(2) With fixed O&M converted				Gas Price								5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems				Boiler Efficiency								85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines

						Exchange Rate Conversion										1.5		CD$/US$





tab25

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300		77.43		74.18		69.34

				Reciprocating engines		2500		59.81		57.01		52.58

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





lgcalc

		

								MW

		Small				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

		Large

		AGRA Monenco est				2328

		Plus 5%				2444.4		122.22		488.88		611.1		611.1		488.88		122.22										2444.4

		yearly shares						0.05		0.2		0.25		0.25		0.2		0.05										1

		Total potential				11214		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676

		Analytical estimate

		Potential % total				0.2179851087		0.225		0.23		0.235		0.24		0.25		0.26		0.27		0.28		0.29		0.3

		Penetration curve						5		8		15		15		11		10		9		8		8		8		97

		cogeneration installed						128		212		411		425		329		315		298		278		291		304		2990.4633105548

		Market timing - small : from Steve Williams

		%accessible						0.016		0.0301		0.046		0.0588		0.0572		0.055		0.0522		0.0464		0.0464		0.0464

		%exposed						4		7		10		12		11		10		9		8		8		8		87

		%targetable						40		43		46		49		52		55		58		58		58		58

		Market timing - large

		%accessible						2.5%		4.1%		6.2%		8.3%		6.3%		5.4%		5.0%		5.1%		5.3%		5.4%

		%exposed						5		8		12		15		11		9		8		8		8		8		92

		%targetable						50		51		52		55		57		60		62		64		66		68

		%success						0.4		0.4		0.4		0.45		0.45		0.45		0.5		0.5		0.5		0.55

								113.6416843299		187.9203420968		291.1655199732		438.6631961191		337.6320346218		294.2323132615		303.8061806452		317.239623437		330.9001439422		379.2665163771		2994.4675548038

																																				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL								2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895

		AGRA Monenco pot				2328																										AGRA Monenco pot				2858																										AGRA Monenco pot				1500

		plus 5%				2444.4																										plus 5%				3000.9																										plus 5%				1575

		Potential % total				0.2179851087		0.2179851087		0.2229851087		0.2279851087		0.2329851087		0.2379851087		0.2429851087		0.2479851087		0.2529851087		0.2629851087		0.2729851087						Potential % total				0.2676123027		0.2676123027		0.2776123027		0.2876123027		0.2976123027		0.3076123027		0.3176123027		0.3276123027		0.3376123027		0.3526123027		0.3676123027						Potential % total				0.1404543226		0.1404543226		0.1437543226		0.1470543226		0.1503543226		0.1536543226		0.1569543226		0.1602543226		0.1635543226		0.1710543226		0.1785543226

		Potential						2477.2194916315		2567.6126174837		2659.5113274477		2752.9156215234		2847.8254997109		2942.1428244176		3037.8793848338		3135.0351809594		3296.2806946017		3460.3646796628		3002.1926028449				Potential						3041.1912831111		3196.6298346639		3355.0795544401		3516.5404424397		3681.0124986628		3845.75319162		4013.3323559959		4183.7499917907		4419.6765808115		4659.8608769606		3982.1577229956				Potential						1596.1465796594		1655.2917579046		1715.4306216635		1776.5631709362		1838.6894057226		1900.4540505232		1963.155390892		2026.7934268291		2144.0113630524		2263.3581528399		1943.5699875476

		Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99

		cogeneration installed - one curve						99		154		532		358		285		441		304		251		231		208		2861.9830889976				cogeneration installed - one curve						122		192		671		457		368		577		401		335		309		280		3711.578086636				cogeneration installed - one curve						64		99		343		231		184		285		196		162		150		136		1850.4810511854

		diff								90.3931258523		91.898709964		93.4042940757		94.9098781874		94.3173247068		95.7365604162		97.1557961256		161.2455136423		164.0839850611		983.1451880314				diff								155.4385515528		158.4497197762		161.4608879997		164.4720562231		164.7406929571		167.5791643759		170.4176357948		235.9265890208		240.1842961491		1618.6695938495				diff								59.1451782452		60.1388637589		61.1325492727		62.1262347864		61.7646448006		62.7013403688		63.638035937		117.2179362233		119.3467897875		667.2115731804

								2444.4																				2444.4										3000.9																				3000.9										1575																				1575

		Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100

		Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100

		Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100

		Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100

		Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100

		Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90

		Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70

		Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45

		Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20

		Penetration curve 10																								5						Penetration curve 10																								5						Penetration curve 10																								5

		Install 1				48.888		73.332		366.66		488.88		488.88		611.1		244.44		122.22								2444.4				Install 1				60.018		90.027		450.135		600.18		600.18		750.225		300.09		150.045								3000.9				Install 1				31.5		47.25		236.25		315		315		393.75		157.5		78.75								1575

		Install 2								4.5196562926		18.0786251705		22.5982814631		22.5982814631		18.0786251705		4.5196562926								90.3931258523				Install 2								7.7719275776		31.0877103106		38.8596378882		38.8596378882		31.0877103106		7.7719275776								155.4385515528				Install 2								2.9572589123		11.829035649		14.7862945613		14.7862945613		11.829035649		2.9572589123								59.1451782452

		Install 3										4.5949354982		18.3797419928		22.974677491		22.974677491		18.3797419928		4.5949354982						91.898709964				Install 3										7.9224859888		31.6899439552		39.6124299441		39.6124299441		31.6899439552		7.9224859888						158.4497197762				Install 3										3.0069431879		12.0277727518		15.0347159397		15.0347159397		12.0277727518		3.0069431879						60.1388637589

		Install 4												4.6702147038		18.6808588151		23.3510735189		23.3510735189		18.6808588151		4.6702147038				93.4042940757				Install 4												8.0730444		32.2921775999		40.3652219999		40.3652219999		32.2921775999		8.0730444				161.4608879997				Install 4												3.0566274636		12.2265098545		15.2831373182		15.2831373182		12.2265098545		3.0566274636				61.1325492727

		Install 5														4.7454939094		18.9819756375		23.7274695469		23.7274695469		18.9819756375		4.7454939094		94.9098781874				Install 5														8.2236028112		32.8944112446		41.1180140558		41.1180140558		32.8944112446		8.2236028112		164.4720562231				Install 5														3.1063117393		12.4252469573		15.5315586966		15.5315586966		12.4252469573		3.1063117393		62.1262347864

		Install 6																4.7158662353		14.147598706		23.5793311767		23.5793311767		18.8634649414		84.8855922361				Install 6																8.2370346479		24.7111039436		41.1851732393		41.1851732393		32.9481385914		148.2666236614				Install 6																3.08823224		9.2646967201		15.4411612002		15.4411612002		12.3529289601		55.5881803206

		Install 7																		4.7868280208		14.3604840624		23.934140104		23.934140104		67.0155922913				Install 7																		8.3789582188		25.1368746564		41.894791094		41.894791094		117.3054150632				Install 7																		3.1350670184		9.4052010553		15.6753350922		15.6753350922		43.8909382582

		Install 8																				4.8577898063		14.5733694188		24.2889490314		43.7201082565				Install 8																				8.5208817897		25.5626453692		42.6044089487		76.6879361076				Install 8																				3.1819017969		9.5457053906		15.9095089843		28.6371161717

		Install 9																						8.0622756821		24.1868270463		32.2491027285				Install 9																						11.796329451		35.3889883531		47.1853178042				Install 9																						5.8608968112		17.5826904335		23.4435872447

		Install 10																								8.2041992531		8.2041992531				Install 10																								12.0092148075		12.0092148075				Install 10																								5.9673394894		5.9673394894

						48.888		73.332		371.1796562926		511.5535606687		534.5282381597		680.0993116786		332.5422180532		211.132368078		89.8008689056		93.801306723		104.2230742856		3002.1926028449								60.018		90.027		457.9069275776		639.1901962994		678.8026262434		869.2128482433		452.286808147		304.0801697509		156.1756073299		161.4063947981		173.0691446058		3982.1577229956								31.5		47.25		239.2072589123		329.835978837		344.8706947767		438.9038320949		215.1603681042		136.9494914173		58.7932757914		62.004972915		70.5941146988		1943.5699875476





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		85%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																above (cols. N,O): total MW if elec limited, with 250 MW or 18 MW units																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"





tab44

		

						Estimated Economic Cogeneration Installed Annually

						Large and Medium Scale Applications

						Base Case

								MW Installed in Year

																														Cumulative

										2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential				73		493		634		657		558		210		89		90		94		104		3002





tab 47

		

						Estimated Economic Cogeneration Installed Annually

						High and Low Cases

								MW Installed in Year

						HIGH CASE (Low gas prices)																						Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		90		458		639		679		869		452		304		156		161		173		3982

						Small		65		72		78		85		100		133		132		137		158		177		1136

						TOTAL		155		529		717		763		969		585		436		293		319		350		5118

						LOW CASE High gas prices)

						Large/Medium		47		239		330		345		439		215		137		59		62		71		1944

						Small		34		37		40		44		48		51		65		75		90		105		588

						TOTAL		81		276		370		388		487		266		202		134		152		176		2532





tab46

		

						Estimated Economic Cogeneration Installed Annually

						Base Case

								MW Installed in Year

																												Cumulative

						Scale		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		73		493		634		657		558		210		89		90		94		104		3002

						Small		50		55		60		65		72		88		119		122		123		125		879

						TOTAL		123		548		694		722		630		298		208		212		217		229		3881





tab45

								MW

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

						Estimated Economic Cogeneration Installed Annually

						Small Scale Applications

						Base Case

								MW Installed in Year

																												Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential		50		55		60		65		72		88		119		122		123		125		879





tab42

		

				Economic Potential

				Large and Medium Scale

				Returns at $50 per MWh.

				Type of Unit				Rated Output				IRR

								(MW)				(%)

				Cogeneration

						Gas Turbine		CCC		250		25.47

								SCC		250		43.57

								CCC		150		18.62

								CCC		100		N/A

								CCC		50		N/A

								SCC		40		N/A

								SCC		26		N/A

								SCC		10		N/A

				IRR = Internal Rate of Return

				IRR computed with electricity rate

						at 50.00 Cdn$/MWh





tab32_5

		

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		2537		13750

				2005		11966		31.06				2005		11966		2483		14449

				2010		12676		33.09				2010		12676		2461		15138

				2015		13371		34.96				2015		13371		2448		15819

				2020		14037		36.44				2020		14037		2477		16514





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts

0

0

0

0

0

0

0

0

0

0

0

0



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible






_1028468809.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

								Cost

				Type		Size				($/MWh)

						(MW)		2000		2005		2010

				CCC		250		47.24		45.79		44.34

				CCC		50		74.61		73.06		71.51





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls				Capacity Factor								90%

		(2) With fixed O&M converted				Gas Price								5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems				Boiler Efficiency								85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines

						Exchange Rate Conversion										1.5		CD$/US$





tab25

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300		77.43		74.18		69.34

				Reciprocating engines		2500		59.81		57.01		52.58

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





lgcalc

		

								MW

		Small				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

		Large

		AGRA Monenco est				2328

		Plus 5%				2444.4		122.22		488.88		611.1		611.1		488.88		122.22										2444.4

		yearly shares						0.05		0.2		0.25		0.25		0.2		0.05										1

		Total potential				11214		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676

		Analytical estimate

		Potential % total				0.2179851087		0.225		0.23		0.235		0.24		0.25		0.26		0.27		0.28		0.29		0.3

		Penetration curve						5		8		15		15		11		10		9		8		8		8		97

		cogeneration installed						128		212		411		425		329		315		298		278		291		304		2990.4633105548

		Market timing - small : from Steve Williams

		%accessible						0.016		0.0301		0.046		0.0588		0.0572		0.055		0.0522		0.0464		0.0464		0.0464

		%exposed						4		7		10		12		11		10		9		8		8		8		87

		%targetable						40		43		46		49		52		55		58		58		58		58

		Market timing - large

		%accessible						2.5%		4.1%		6.2%		8.3%		6.3%		5.4%		5.0%		5.1%		5.3%		5.4%

		%exposed						5		8		12		15		11		9		8		8		8		8		92

		%targetable						50		51		52		55		57		60		62		64		66		68

		%success						0.4		0.4		0.4		0.45		0.45		0.45		0.5		0.5		0.5		0.55

								113.6416843299		187.9203420968		291.1655199732		438.6631961191		337.6320346218		294.2323132615		303.8061806452		317.239623437		330.9001439422		379.2665163771		2994.4675548038

																																				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL								2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895

		AGRA Monenco pot				2328																										AGRA Monenco pot				2858																										AGRA Monenco pot				1500

		plus 5%				2444.4																										plus 5%				3000.9																										plus 5%				1575

		Potential % total				0.2179851087		0.2179851087		0.2229851087		0.2279851087		0.2329851087		0.2379851087		0.2429851087		0.2479851087		0.2529851087		0.2629851087		0.2729851087						Potential % total				0.2676123027		0.2676123027		0.2776123027		0.2876123027		0.2976123027		0.3076123027		0.3176123027		0.3276123027		0.3376123027		0.3526123027		0.3676123027						Potential % total				0.1404543226		0.1404543226		0.1437543226		0.1470543226		0.1503543226		0.1536543226		0.1569543226		0.1602543226		0.1635543226		0.1710543226		0.1785543226

		Potential						2477.2194916315		2567.6126174837		2659.5113274477		2752.9156215234		2847.8254997109		2942.1428244176		3037.8793848338		3135.0351809594		3296.2806946017		3460.3646796628		3002.1926028449				Potential						3041.1912831111		3196.6298346639		3355.0795544401		3516.5404424397		3681.0124986628		3845.75319162		4013.3323559959		4183.7499917907		4419.6765808115		4659.8608769606		3982.1577229956				Potential						1596.1465796594		1655.2917579046		1715.4306216635		1776.5631709362		1838.6894057226		1900.4540505232		1963.155390892		2026.7934268291		2144.0113630524		2263.3581528399		1943.5699875476

		Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99

		cogeneration installed - one curve						99		154		532		358		285		441		304		251		231		208		2861.9830889976				cogeneration installed - one curve						122		192		671		457		368		577		401		335		309		280		3711.578086636				cogeneration installed - one curve						64		99		343		231		184		285		196		162		150		136		1850.4810511854

		diff								90.3931258523		91.898709964		93.4042940757		94.9098781874		94.3173247068		95.7365604162		97.1557961256		161.2455136423		164.0839850611		983.1451880314				diff								155.4385515528		158.4497197762		161.4608879997		164.4720562231		164.7406929571		167.5791643759		170.4176357948		235.9265890208		240.1842961491		1618.6695938495				diff								59.1451782452		60.1388637589		61.1325492727		62.1262347864		61.7646448006		62.7013403688		63.638035937		117.2179362233		119.3467897875		667.2115731804

								2444.4																				2444.4										3000.9																				3000.9										1575																				1575

		Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100

		Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100

		Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100

		Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100

		Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100

		Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90

		Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70

		Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45

		Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20

		Penetration curve 10																								5						Penetration curve 10																								5						Penetration curve 10																								5

		Install 1				48.888		73.332		366.66		488.88		488.88		611.1		244.44		122.22								2444.4				Install 1				60.018		90.027		450.135		600.18		600.18		750.225		300.09		150.045								3000.9				Install 1				31.5		47.25		236.25		315		315		393.75		157.5		78.75								1575

		Install 2								4.5196562926		18.0786251705		22.5982814631		22.5982814631		18.0786251705		4.5196562926								90.3931258523				Install 2								7.7719275776		31.0877103106		38.8596378882		38.8596378882		31.0877103106		7.7719275776								155.4385515528				Install 2								2.9572589123		11.829035649		14.7862945613		14.7862945613		11.829035649		2.9572589123								59.1451782452

		Install 3										4.5949354982		18.3797419928		22.974677491		22.974677491		18.3797419928		4.5949354982						91.898709964				Install 3										7.9224859888		31.6899439552		39.6124299441		39.6124299441		31.6899439552		7.9224859888						158.4497197762				Install 3										3.0069431879		12.0277727518		15.0347159397		15.0347159397		12.0277727518		3.0069431879						60.1388637589

		Install 4												4.6702147038		18.6808588151		23.3510735189		23.3510735189		18.6808588151		4.6702147038				93.4042940757				Install 4												8.0730444		32.2921775999		40.3652219999		40.3652219999		32.2921775999		8.0730444				161.4608879997				Install 4												3.0566274636		12.2265098545		15.2831373182		15.2831373182		12.2265098545		3.0566274636				61.1325492727

		Install 5														4.7454939094		18.9819756375		23.7274695469		23.7274695469		18.9819756375		4.7454939094		94.9098781874				Install 5														8.2236028112		32.8944112446		41.1180140558		41.1180140558		32.8944112446		8.2236028112		164.4720562231				Install 5														3.1063117393		12.4252469573		15.5315586966		15.5315586966		12.4252469573		3.1063117393		62.1262347864

		Install 6																4.7158662353		14.147598706		23.5793311767		23.5793311767		18.8634649414		84.8855922361				Install 6																8.2370346479		24.7111039436		41.1851732393		41.1851732393		32.9481385914		148.2666236614				Install 6																3.08823224		9.2646967201		15.4411612002		15.4411612002		12.3529289601		55.5881803206

		Install 7																		4.7868280208		14.3604840624		23.934140104		23.934140104		67.0155922913				Install 7																		8.3789582188		25.1368746564		41.894791094		41.894791094		117.3054150632				Install 7																		3.1350670184		9.4052010553		15.6753350922		15.6753350922		43.8909382582

		Install 8																				4.8577898063		14.5733694188		24.2889490314		43.7201082565				Install 8																				8.5208817897		25.5626453692		42.6044089487		76.6879361076				Install 8																				3.1819017969		9.5457053906		15.9095089843		28.6371161717

		Install 9																						8.0622756821		24.1868270463		32.2491027285				Install 9																						11.796329451		35.3889883531		47.1853178042				Install 9																						5.8608968112		17.5826904335		23.4435872447

		Install 10																								8.2041992531		8.2041992531				Install 10																								12.0092148075		12.0092148075				Install 10																								5.9673394894		5.9673394894

						48.888		73.332		371.1796562926		511.5535606687		534.5282381597		680.0993116786		332.5422180532		211.132368078		89.8008689056		93.801306723		104.2230742856		3002.1926028449								60.018		90.027		457.9069275776		639.1901962994		678.8026262434		869.2128482433		452.286808147		304.0801697509		156.1756073299		161.4063947981		173.0691446058		3982.1577229956								31.5		47.25		239.2072589123		329.835978837		344.8706947767		438.9038320949		215.1603681042		136.9494914173		58.7932757914		62.004972915		70.5941146988		1943.5699875476





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		85%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																above (cols. N,O): total MW if elec limited, with 250 MW or 18 MW units																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"





tab44

		

						Estimated Economic Cogeneration Installed Annually

						Large and Medium Scale Applications

						Base Case

						MW Installed in Year

																														Cumulative

										2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential				73		493		634		657		558		210		89		90		94		104		3002





tab 47

		

						Estimated Economic Cogeneration Installed Annually

						High and Low Cases

								MW Installed in Year

						HIGH CASE (Low gas prices)																						Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		90		458		639		679		869		452		304		156		161		173		3982

						Small		65		72		78		85		100		133		132		137		158		177		1136

						TOTAL		155		529		717		763		969		585		436		293		319		350		5118

						LOW CASE High gas prices)

						Large/Medium		47		239		330		345		439		215		137		59		62		71		1944

						Small		34		37		40		44		48		51		65		75		90		105		588

						TOTAL		81		276		370		388		487		266		202		134		152		176		2532





tab46

		

						Estimated Economic Cogeneration Installed Annually

						Base Case

								MW Installed in Year

																												Cumulative

						Scale		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		73		493		634		657		558		210		89		90		94		104		3002

						Small		50		55		60		65		72		88		119		122		123		125		879

						TOTAL		123		548		694		722		630		298		208		212		217		229		3881





tab45

								MW

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

						Estimated Economic Cogeneration Installed Annually

						Small Scale Applications

						Base Case

								MW Installed in Year

																												Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential		50		55		60		65		72		88		119		122		123		125		879





tab42

		

				Economic Potential

				Large and Medium Scale

				Returns at $50 per MWh.

				Type of Unit				Rated Output				IRR

								(MW)				(%)

				Cogeneration

						Gas Turbine		CCC		250		25.47

								SCC		250		43.57

								CCC		150		18.62

								CCC		100		N/A

								CCC		50		N/A

								SCC		40		N/A

								SCC		26		N/A

								SCC		10		N/A

				IRR = Internal Rate of Return

				IRR computed with electricity rate

						at 50.00 Cdn$/MWh





tab32_5

		

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		2537		13750

				2005		11966		31.06				2005		11966		2483		14449

				2010		12676		33.09				2010		12676		2461		15138

				2015		13371		34.96				2015		13371		2448		15819

				2020		14037		36.44				2020		14037		2477		16514





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts

0

0

0

0

0

0

0

0

0

0

0

0



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible






_1028449450.xls
tab 48

		

						GHG EMISSION SAVINGS FROM COGENERATION

						BASE CASE

						Mtons CO2

																										Cumulative

						2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Totals

		Emissions from Cogeneration

				Large Applications		0.2		1.7		3.6		5.6		7.3		8.7		9.0		9.3		9.6		10.0		65.1

				Small Applications		0.1		0.3		0.5		0.8		1.2		1.6		2.0		2.5		2.9		3.4		15.3

		TOTAL EMISSIONS				0.3		2.0		4.1		6.4		8.5		10.3		11.0		11.8		12.6		13.4		80.3

		Avoided Emissions

				Electricity Generation		0.8		5.1		10.6		16.5		21.8		24.3		25.9		27.6		29.3		31.2		193.1

				Heat Production		0.2		0.8		1.6		2.5		3.3		4.7		5.3		5.8		5.5		6.0		35.6

		TOTAL AVOIDED				1.0		5.9		12.2		19.0		25.1		29.0		31.2		33.4		34.8		37.2		228.8

		NET EMISSION REDUCTION				0.6		3.9		8.1		12.6		16.7		18.7		20.2		21.6		22.2		23.8		148.4





eleclg

		

		GHG emissions by large scale generators

						2001		2002		2003		2004		2005		2006		2007		2008		2009		2010

		Installed in year				73		493		634		657		558		210		89		90		94		104										8652

		Cumulative				73		567		1201		1857		2415		2625		2714		2804		2898		3002										10815

																																		11,124

		Capacity factor				0.93		0.93		0.93		0.93		0.93		0.93		0.93		0.93		0.93		0.93

																										HEAT RATES (BTU/KWH)

		MWh generated				597421		4617049		9780276		15130672		19675604		21389057		22113408		22844998		23609178		24458263				wtd				wtd

																										wts last 5				wts first 5 yrs				plant		electricity

		Average heat rates				7038		7038		7038		7038		7038		7784		7784		7784		7784		7784		0.5		3352.65		0.67		4492.551		6,705		4,330		SCC 250

																										0.25		1928.675		0.33		2545.851		7,715		< 6,000		CCC 150

		TOTAL BTU(X10^9)				4205		32497		68838		106496		138485		166497		172136		177831		183779		190389		0.1		865.2				0		8652		4,350		SCC		40

																										0.1		1081.5				0		10815		4,840		SCC		26

		TOTAL TJ				4437		34287		72630		112364		146115		175671		181620		187629		193905		200879		0.05		556.2				0		11,124		4,780		SCC		10

																										1		7784.225		1		7038.402

		CO2 Mtons/				0.2		1.7		3.6		5.6		7.3		8.7		9.0		9.3		9.6		10.0

				capfaclg		0.93		average capacity factor for large generation

				JBtu		1055.1		joules/btu

				tco2		49.68		tons of CO2 per TJ, from NRCan 2020





coal elec

		

						2001		2002		2003		2004		2005		2006		2007		2008		2009		2010				CO2 KG/MWh

		Avoided by large applications																										late				early

		MWh generated				597421		4617049		9780276		15130672		19675604		21389057		22113408		22844998		23609178		24458263				wts				wts

		CO2 from coal plants																								174		0.2		130.5		0.15		870		Lambton 3/4

				Mtonnes		0.5		4.1		8.8		13.6		17.7		19.2		19.8		20.5		21.2		21.9		0		0		90.6		0.1		906		Thunder Bay

																										150		0.15		100		0.1		1000		Atikokan

				Mtons		0.5906130458		4.5644344853		9.6688218334		14.9582463311		19.4513843808		21.1453112586		21.8614079765		22.5846606452		23.3401326828		24.1795412268		396		0.45		352		0.4		880		Nanticoke

																										176		0.2		132		0.15		880		Lambton 1/2

		Avoided by small applications																								0		0		92		0.1		920		Lakeview

		MWh generated

				Gas turbines		157680		412216		774049		1253371		1872351		2460051		3193720		3940969		4689387		5444937		896		1		897.1		1

				Diesel reciprocating		39420		101784		188662		301378		443771		574198		732440		889756		1043404		1194514

				Fuel cells		0		3388		12935		31906		64846		108839		175973		254630		343846		444586

				TOTAL		197100		517388		975645		1586655		2380968		3143088		4102133		5085355		6076637		7084037

		CO2 from coal plants

				Mtonnes		0.2		0.5		0.9		1.4		2.1		2.8		3.7		4.6		5.5		6.4

				Mtons		0.1948538878		0.5114914555		0.9645267447		1.568573797		2.3538349649		3.1072699978		4.055385715		5.0274035092		6.0073886624		7.0033085334

		TOTAL AVOIDED				0.7854669336		5.0759259408		10.6333485781		16.526820128		21.8052193456		24.2525812564		25.9167936916		27.6120641544		29.3475213452		31.1828497603





avoided

		

						CO2 emissions avoided by cogeneration applications

						Mtons

																										Cumulative

		For Electricity Generation				2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

		Large Applications				0.6		4.6		9.7		15.0		19.5		21.1		21.9		22.6		23.3		24.2		162.3

		Small Applications				0.2		0.5		1.0		1.6		2.4		3.1		4.1		5.0		6.0		7.0		30.8

		TOTAL ELECTRICITY				0.8		5.1		10.6		16.5		21.8		24.3		25.9		27.6		29.3		31.2		193.1

		For Heat Production

		Large Applications				0.1		0.5		1.1		1.6		2.1		3.1		3.2		3.4		2.5		2.6		20.3

		Small Applications				0.1		0.3		0.5		0.8		1.2		1.6		2.0		2.5		2.9		3.4		15.4

		TOTAL HEAT				0.2		0.8		1.6		2.5		3.3		4.7		5.3		5.8		5.5		6.0		35.6

		Total Displaced CO2				1.0		5.9		12.2		19.0		25.1		29.0		31.2		33.4		34.8		37.2		228.8

		Total Emissions				0.3		2.0		4.1		6.4		8.5		10.3		11.0		11.8		12.6		13.4		80.3

		CO2 Net Reduction				0.6		3.9		8.1		12.6		16.7		18.7		20.2		21.6		22.2		23.8		148.4





CGNEMIT

		

						CO2 emitted by cogeneration applications

						Mtons

		SMALL APPLICATIONS

		Application				2001		2002		2003		2004		2005		2006		2007		2008		2009		2010

		Gas turbines				0.1		0.2		0.4		0.6		0.9		1.2		1.5		1.9		2.2		2.6

		Diesel reciprocating				0.0233300224		0.0598972277		0.1103896091		0.1753307413		0.2566799715		0.3292248797		0.4162625839		0.5011825352		0.5824691059		0.6608019272

		Fuel cells				0		0.0012117515		0.0046266875		0.0114124959		0.0231951268		0.0389314653		0.0629447276		0.0910803145		0.1229922968		0.1590266039

		TOTAL				0.1		0.3		0.5		0.8		1.2		1.6		2.0		2.5		2.9		3.4		15.3

		LARGE APPLICATIONS

		Gas turbines				0.2		1.7		3.6		5.6		7.3		8.7		9.0		9.3		9.6		10.0		65.1

		TOTAL EMISSIONS				0.3		2.0		4.1		6.4		8.5		10.3		11.0		11.8		12.6		13.4		80.3





elecsm

		

						2001		2002		2003		2004		2005		2006		2007		2008		2009		2010

		Installed in year				50		55		60		65		72		88		119		122		123		125

		Cumulative				50		105		165		230		302		390		509		631		754		879

																																								Heat rates (Btu/kWh)

		for natural gas fired small generation

																										2000								2005								2010

																												wts		wts						wts		wts						wts		wts

		Year share of total				0.8		0.79375		0.7875		0.78125		0.775		0.77		0.765		0.76		0.755		0.75		wtd ht rate		%gas		%total				wtd ht rate		%gas		%total						%gas		%total

		Installed in year				40		43.65625		47.25		50.78125		55.8		67.76		91.035		92.72		92.865		93.75

		Cumulative				40		84		131		182		237		305		396		489		582		676		0				0		6824		0				0.05		6,824		0				0.1		6,824		900		Solid Oxide-Atmos. Hybrid

																										710.8125		0.0625		0.05		11373		1420.1290322581		0.1290322581		0.1		11006		2067.8		0.2		0.15		10339		100		Microturbine

		Capacity factor				0.45		0.5625		0.675		0.7875		0.9		0.92		0.92		0.92		0.92		0.92		0				0.2		7935		0				0.175		7755		0				0.15		7417		2500		Reciprocating engines

																										1854.25		0.25		0.2		7417		1796.9032258065		0.2580645161		0.2		6963		1592.2666666667		0.2333333333		0.175		6824		5000		Reciprocating engines

		MWh generated				157680		412216		774049		1253371		1872351		2460051		3193720		3940969		4689387		5444937		2284.875		0.1875		0.15		12186		1518.1935483871		0.1290322581		0.1		11,766		1516.4		0.1333333333		0.1		11,373		1500		aero turbine

																										2584.75		0.25		0.2		10339		2201.3870967742		0.2258064516		0.175		9,749		1844.4		0.2		0.15		9,222		3000		aero turbine

		Average heat rates				9871.9375		9733.0740927419		9594.2106854839		9455.3472782258		9316.4838709677		9255.4270967742		9194.3703225806		9133.3135483871		9072.2567741936		9011.2		2437.25		0.25		0.2		9749		2379.8709677419		0.2580645161		0.2		9,222		1990.3333333333		0.2333333333		0.175		8,530		6000		aero turbine

		Electricity Calculation																								9871.9375		1		1				9316.4838709677		1		1				9011.2		1		1

		TOTAL BTU(X10^9) elec				1557		4012		7426		11851		17444		22769		29364		35994		42543		49065						0.8								0.775								0.75						nat gas share

																														0.2								0.175								0.15						diesel share

		TOTAL TJ				1642		4233		7836		12504		18405		24023		30982		37977		44887		51769

																																								steam generated

		CO2 Mtons				0.1		0.2		0.4		0.6		0.9		1.2		1.5		1.9		2.2		2.6		2000								2005								2010

		Displaced heat calculation																								wtd		wts		wts				wtd		wts		wts				wtd		wts		wts		E/T ratio

		average e/t				0.73125		0.7403729839		0.7494959677		0.7586189516		0.7677419355		0.7719268817		0.776111828		0.7802967742		0.7844817204		0.7886666667

		TOTAL BTU(X10^9) heat				2128.6934769231		5419.0666467985		9908.5067945759		15621.8877957343		22720.827505292		29496.0831176288		37835.0678730893		46128.7375226456		54231.1157054851		62213.1178699415

		End use BTU				1809.3894553846		4606.2066497787		8422.2307753895		13278.6046263742		19312.7033794982		25071.6706499845		32159.8076921259		39209.4268942488		46096.4483496623		52881.1501894503

		TOTAL TJ heat				1909		4860		8886		14010		20377		26453		33932		41370		48636		55795

		CO2 Mtons heat				0.1		0.2		0.4		0.7		1.0		1.3		1.7		2.1		2.4		2.8

																										E/T ratio		%gas		%total		E/T ratio		E/T ratio		%gas		%total		E/T ratio		E/T ratio		%gas		%total

		for diesel fired small generation

																										0				0		2.0		0				0.05		2.0		0				0.1		2.0		900		Solid Oxide-Atmos. Hybrid

		Year share of total				0.2		0.19375		0.1875		0.18125		0.175		0.17		0.165		0.16		0.155		0.15		0.0375		0.0625		0.05		0.6		0.0774193548		0.1290322581		0.1		0.6		0.14		0.2		0.15		0.7		100		Microturbine

		Installed in year				10		10.65625		11.25		11.78125		12.6		14.96		19.635		19.52		19.065		18.75		0				0.2		1.1		0				0.175		1.1		0				0.15		1.1		2500		Reciprocating engines

		Cumulative				10		21		32		44		56		71		91		110		129		148		0.3		0.25		0.2		1.2		0.335483871		0.2580645161		0.2		1.3		0.3033333333		0.2333333333		0.175		1.3		5000		Reciprocating engines

																										0.09375		0.1875		0.15		0.5		0.064516129		0.1290322581		0.1		0.5		0.0666666667		0.1333333333		0.1		0.5		1500		aero turbine

		Capacity factor				0.45		0.5625		0.675		0.7875		0.9		0.92		0.92		0.92		0.92		0.92		0.15		0.25		0.2		0.6		0.135483871		0.2258064516		0.175		0.6		0.12		0.2		0.15		0.6		3000		aero turbine

																										0.15		0.25		0.2		0.6		0.1548387097		0.2580645161		0.2		0.6		0.1586666667		0.2333333333		0.175		0.7		6000		aero turbine

		MWh generated				39420		101784		188662		301378		443771		574198		732440		889756		1043404		1194514		0.73125		1		1				0.7677419355		1		1				0.7886666667		1		1

																														0.8								0.775								0.75

		Average heat rates				7935		7890		7845		7800		7755		7687.4		7619.8		7552.2		7484.6		7417						0.2								0.175								0.15

		TOTAL BTU(X10^9)				313		803		1480		2351		3441		4414		5581		6720		7809		8860

		TOTAL TJ				330		847		1562		2480		3631		4657		5889		7090		8240		9348

		CO2 Mtons				0.0		0.1		0.1		0.2		0.3		0.3		0.4		0.5		0.6		0.7

		Displaced heat calculation

		average e/t				1.1		1.1		1.1		1.1		1.1		1.1		1.1		1.1		1.1		1.1

		TOTAL BTU(X10^9) heat				284.3615454545		730.0665191761		1345.5006302557		2137.0455511364		3128.5830825		4012.8077886044		5073.6801556647		6108.7399674742		7099.5137646087		8054.2853349927

		End use BTU				241.7073136364		620.5565412997		1143.6755357173		1816.4887184659		2659.295620125		3410.8866203137		4312.628132315		5192.4289723531		6034.5866999174		6846.1425347438

		TOTAL TJ heat				255		655		1207		1917		2806		3599		4550		5479		6367		7223

		CO2 Mtons heat				0.0		0.0		0.1		0.1		0.2		0.3		0.3		0.4		0.5		0.5

		for fuel cells

		Year share of total				0		0.0125		0.025		0.0375		0.05		0.06		0.07		0.08		0.09		0.1

		Installed in year				0		0.6875		1.5		2.4375		3.6		5.28		8.33		9.76		11.07		12.5

		Cumulative				0		1		2		5		8		14		22		32		43		55

		Capacity factor				0.45		0.5625		0.675		0.7875		0.9		0.92		0.92		0.92		0.92		0.92

		MWh generated				0		3388		12935		31906		64846		108839		175973		254630		343846		444586

		Average heat rates				6824		6824		6824		6824		6,824		6824		6824		6824		6824		6,824

		TOTAL BTU(X10^9)				0		23		88		218		443		743		1201		1738		2346		3034

		TOTAL TJ				0		24		93		230		467		784		1267		1833		2476		3201

		CO2 Mtons				0.0		0.0		0.0		0.0		0.0		0.0		0.1		0.1		0.1		0.2

		Displaced heat calculation

		average e/t				2.0		2		2		2		2.0		2		2		2		2		2.0

		TOTAL BTU(X10^9) heat				0		11.558683125		44.13315375		108.86177925		221.2542108		371.360360352		600.418620384		868.799006688		1173.201760416		1516.926640416

		End use BTU				0		9.8248806563		37.5131806875		92.5325123625		188.06607918		315.6563062992		510.3558273264		738.4791556848		997.2214963536		1289.3876443536

		TOTAL TJ heat				0		10		40		98		198		333		538		779		1052		1360

		CO2 Mtons heat fuel cell				0.00		0.00		0.00		0.00		0.01		0.02		0.03		0.04		0.05		0.07

		CO2 Mtons heat diesel				0.02		0.05		0.09		0.14		0.20		0.25		0.32		0.39		0.45		0.51

		CO2 Mtons heat turbines				0.09		0.24		0.44		0.70		1.01		1.31		1.69		2.06		2.42		2.77

		TOTAL HEAT DISPL				0.11		0.29		0.53		0.84		1.22		1.59		2.03		2.48		2.92		3.35

						dco2		70.69		co2 per unit diesel

						effsm		0.85





gas boil

		

		Steam use for large-scale applications

						2001		2002		2003		2004		2005		2006		2007		2008		2009		2010

		Installed MW				73		567		1201		1857		2415		2625		2714		2804		2898		3002

		Capacity factor				0.93		0.93		0.93		0.93		0.93		0.93		0.93		0.93		0.93		0.93

																										Net HEAT RATES (BTU/KWH)

		TOTAL BTU(X10^9)				1309		10113		21422		33141		43096		63873		66036		68220		51711		53571		Calculation for steam requirement

																												wtd				wtd

		TOTAL TJ				1381		10670		22602		34967		45470		67392		69674		71979		54561		56523		wts last 5				wts first 5 yrs				plant		electricity		diff

																										0.5		1187.65		0.67		1591.451		6,705		4,330		2,375		SCC 250

		CO2 Mtons				0.1		0.5		1.1		1.7		2.3		3.3		3.5		3.6		2.7		2.8		0.25		453.675		0.33		598.851		7,715		< 6,000		1,815		CCC 150

																										0.1		430.2				0		8652		4,350		4,302		SCC		40

		End use BTU				981.3995343957		7584.5494956207		16066.3184007712		24855.5565934437		32321.6354775644		47904.4018171176		49526.7087435341		51165.2273745521		38783.4225988783		40178.236276088		0.1		597.5				0		10815		4,840		5,975		SCC		26

																										0.05		317.2				0		11,124		4,780		6,344		SCC		10

		Input BTU from boiler				1226.7494179946		9480.6868695259		20082.8980009641		31069.4457418046		40402.0443469555		59880.502271397		61908.3859294176		63956.5342181902		48479.2782485978		50222.79534511		1		2986.225		1		2190.302

		TOTAL TJ				1294		10003		21189		32781		42628		63180		65320		67481		51150		52990

		CO2 Mtons				0.1		0.5		1.1		1.6		2.1		3.1		3.2		3.4		2.5		2.6

																																								Heat rates (Btu/kWh)

																										2000		wts		wts				2005		wts		wts				2010		wts		wts

																										wtd ht rate		%gas		%total				wtd ht rate		%gas		%total						%gas		%total

																										0				0		6824		0				0.05		6,824		0				0.1		6,824		900		Solid Oxide-Atmos. Hybrid

																										710.8125		0.0625		0.05		11373		1420.1290322581		0.1290322581		0.1		11006		2067.8		0.2		0.15		10339		100		Microturbine

																										0				0.2		7935		0				0.175		7755		0				0.15		7417		2500		Reciprocating engines

																										1854.25		0.25		0.2		7417		1796.9032258065		0.2580645161		0.2		6963		1592.2666666667		0.2333333333		0.175		6824		5000		Reciprocating engines

																										2284.875		0.1875		0.15		12186		1518.1935483871		0.1290322581		0.1		11,766		1516.4		0.1333333333		0.1		11,373		1500		aero turbine

																										2584.75		0.25		0.2		10339		2201.3870967742		0.2258064516		0.175		9,749		1844.4		0.2		0.15		9,222		3000		aero turbine

																										2437.25		0.25		0.2		9749		2379.8709677419		0.2580645161		0.2		9,222		1990.3333333333		0.2333333333		0.175		8,530		6000		aero turbine

																										9871.9375		1		1				9316.4838709677		1		1				9011.2		1		1

																														0.8								0.775								0.75						nat gas share

																														0.2								0.175								0.15						diesel share

				eff		0.75		efficiency factor for use of heat from cogeneration

				effb		0.8		efficiency factor for steam boiler alternative






_1028448180.xls
Cogen List

		Table 3.1

		Industrial Cogeneration Potential In Ontario

				February 2000

		Project Location		Market Segment		Electrical Capacity (MW)		Probability of Proceeding

		Identified 10-40 MW

		GTA		nug		10		H

		N. Ont.		ind		20		M

		Central Ont.		nug		20		M

		GTA		inst		15		M

		GTA		nug		20		M

		GTA		ind		11		M

		GTA		nug		25		M

		Totals		10		121

		Identified 40-100 MW

		GTA		ind		40		M

		East. Ont.		ind		40		M

		East. Ont.		nug		50		M

		GTA		nug		50		M

		GTA		ind		40		M

		East. Ont.		nug		90		L

		NW Ont. Pulp & Paper		nug		65		M				65

		Totals		8		375

		Identified 100-250 MW

		Ottawa/Carlton Pulp & Paper		nug		153		L				153

		East Ont.		ind		110		M

		GTA		nug		150		M

		GTA		nug		100		M

		East. Ont. Pulp & Paper		nug		180		M				180

		N. Ont.		nug		120		L

		GTA		nug		100		L

		GTA		nug		100		L

		NW Ont. Pulp & Paper		nug		165		L				165

		NW Ont.Pulp & Paper		nug		180		L				180

		Totals		10		1,358

		Identified 250 MW  and larger

		GTA Pulp & paper		ind		250		H				250

		Niag. Penn Pulp & Paper		ind		350		M				350

		West. Ont.		nug		550		H				1343

		Niag. Penn.		nug		350		M

		Totals		4		1,500

		Total		32		3,354

		Plus 20% unidentified				688

		Total potential				4,146

		Notes:

		List of all cogeneration projects identified from data sources

		Market segment includes industrial, commercial, institutional and institutional

		Segment listed as NUG if project proposed by non utility generator

		Project capacity refers to proposed size.

		Projects not necessarily sized by embedded electrical or thermal loads

		Probability of proceeding refers to opinion of data source at the time project identified,

		does not necessarily refer to economic viability

		Additional technical potential of 20% based on subjective estimate





LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel		Capital Cost[1]		Levelized		Levelized		Plant		Class 43		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost		Heat Rate[2]		Heat Rate				Tax[3]		Thermal Credit [4]		Thermal Credit		Thermal Credit [5]

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Cogeneration[6]

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		[1] Excludes Interest during Construction

		[2] Include 3% Degradation.

		[3] Tax cost includes Income Tax only. Capital taxes, GST and municipal taxes are not included.

		[4] LUEC is based on the sales value of steam equal to zero Cdn$/klb

		[5] LUEC is based on the sale value of steam equal to 7.51 Cdn$/klb

		[6] Thermal recovery of CCC plants is designed to just meet the Class 43 heat rate of 6000 Btu/kWh.

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible





table 43

		Table 4.3

		Industrial Cogeneration Potential In Ontario

		Economic Potential at $50/MWh Electricity Price

		Project Location		Market Segment		Electrical Capacity (MW)		Probability of Proceeding

		Identified 100-250 MW

		Ottawa/Carlton Pulp & Paper		nug		153		L

		GTA		nug		150		M

		East. Ont. Pulp & Paper		nug		180		M

		NW Ont. Pulp & Paper		nug		165		L

		NW Ont.Pulp & Paper		nug		180		L

		Totals		5		828

		Identified :250 MW  and larger

		GTA Pulp & paper		ind		250		H

		Niag. Penn Pulp & Paper		ind		350		M

		West. Ont.		nug		550		H

		Niag. Penn.		nug		350		M

		Totals		4		1,500

		Total economic potential				2,328

		Notes:

		List of all cogeneration projects identified from data sources

		Market segment includes industrial, commercial, institutional and institutional

		Segment listed as NUG if project proposed by non utility generator

		Project capacity refers to proposed size.

		Projects not necessarily sized by embedded electrical or thermal loads

		Probability of proceeding refers to opinion of data source at the time project identified,

		does not necessarily refer to economic viability

		Additional technical potential of 20% based on subjective estimate






_1028447157.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

								Cost

				Type		Size				($/MWh)

						(MW)		2000		2005		2010

				CCC		250		47.24		45.79		44.34

				CCC		50		74.61		73.06		71.51





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls				Capacity Factor								90%

		(2) With fixed O&M converted				Gas Price								5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems				Boiler Efficiency								85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines

						Exchange Rate Conversion										1.5		CD$/US$





tab25

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300		77.43		74.18		69.34

				Reciprocating engines		2500		59.81		57.01		52.58

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





lgcalc

		

								MW

		Small				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

		Large

		AGRA Monenco est				2328

		Plus 5%				2444.4		122.22		488.88		611.1		611.1		488.88		122.22										2444.4

		yearly shares						0.05		0.2		0.25		0.25		0.2		0.05										1

		Total potential				11214		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676

		Analytical estimate

		Potential % total				0.2179851087		0.225		0.23		0.235		0.24		0.25		0.26		0.27		0.28		0.29		0.3

		Penetration curve						5		8		15		15		11		10		9		8		8		8		97

		cogeneration installed						128		212		411		425		329		315		298		278		291		304		2990.4633105548

		Market timing - small : from Steve Williams

		%accessible						0.016		0.0301		0.046		0.0588		0.0572		0.055		0.0522		0.0464		0.0464		0.0464

		%exposed						4		7		10		12		11		10		9		8		8		8		87

		%targetable						40		43		46		49		52		55		58		58		58		58

		Market timing - large

		%accessible						2.5%		4.1%		6.2%		8.3%		6.3%		5.4%		5.0%		5.1%		5.3%		5.4%

		%exposed						5		8		12		15		11		9		8		8		8		8		92

		%targetable						50		51		52		55		57		60		62		64		66		68

		%success						0.4		0.4		0.4		0.45		0.45		0.45		0.5		0.5		0.5		0.55

								113.6416843299		187.9203420968		291.1655199732		438.6631961191		337.6320346218		294.2323132615		303.8061806452		317.239623437		330.9001439422		379.2665163771		2994.4675548038

																																				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL								2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895

		AGRA Monenco pot				2328																										AGRA Monenco pot				2858																										AGRA Monenco pot				1500

		plus 5%				2444.4																										plus 5%				3000.9																										plus 5%				1575

		Potential % total				0.2179851087		0.2179851087		0.2229851087		0.2279851087		0.2329851087		0.2379851087		0.2429851087		0.2479851087		0.2529851087		0.2629851087		0.2729851087						Potential % total				0.2676123027		0.2676123027		0.2776123027		0.2876123027		0.2976123027		0.3076123027		0.3176123027		0.3276123027		0.3376123027		0.3526123027		0.3676123027						Potential % total				0.1404543226		0.1404543226		0.1437543226		0.1470543226		0.1503543226		0.1536543226		0.1569543226		0.1602543226		0.1635543226		0.1710543226		0.1785543226

		Potential						2477.2194916315		2567.6126174837		2659.5113274477		2752.9156215234		2847.8254997109		2942.1428244176		3037.8793848338		3135.0351809594		3296.2806946017		3460.3646796628		3002.1926028449				Potential						3041.1912831111		3196.6298346639		3355.0795544401		3516.5404424397		3681.0124986628		3845.75319162		4013.3323559959		4183.7499917907		4419.6765808115		4659.8608769606		3982.1577229956				Potential						1596.1465796594		1655.2917579046		1715.4306216635		1776.5631709362		1838.6894057226		1900.4540505232		1963.155390892		2026.7934268291		2144.0113630524		2263.3581528399		1943.5699875476

		Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99

		cogeneration installed - one curve						99		154		532		358		285		441		304		251		231		208		2861.9830889976				cogeneration installed - one curve						122		192		671		457		368		577		401		335		309		280		3711.578086636				cogeneration installed - one curve						64		99		343		231		184		285		196		162		150		136		1850.4810511854

		diff								90.3931258523		91.898709964		93.4042940757		94.9098781874		94.3173247068		95.7365604162		97.1557961256		161.2455136423		164.0839850611		983.1451880314				diff								155.4385515528		158.4497197762		161.4608879997		164.4720562231		164.7406929571		167.5791643759		170.4176357948		235.9265890208		240.1842961491		1618.6695938495				diff								59.1451782452		60.1388637589		61.1325492727		62.1262347864		61.7646448006		62.7013403688		63.638035937		117.2179362233		119.3467897875		667.2115731804

								2444.4																				2444.4										3000.9																				3000.9										1575																				1575

		Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100

		Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100

		Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100

		Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100

		Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100

		Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90

		Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70

		Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45

		Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20

		Penetration curve 10																								5						Penetration curve 10																								5						Penetration curve 10																								5

		Install 1				48.888		73.332		366.66		488.88		488.88		611.1		244.44		122.22								2444.4				Install 1				60.018		90.027		450.135		600.18		600.18		750.225		300.09		150.045								3000.9				Install 1				31.5		47.25		236.25		315		315		393.75		157.5		78.75								1575

		Install 2								4.5196562926		18.0786251705		22.5982814631		22.5982814631		18.0786251705		4.5196562926								90.3931258523				Install 2								7.7719275776		31.0877103106		38.8596378882		38.8596378882		31.0877103106		7.7719275776								155.4385515528				Install 2								2.9572589123		11.829035649		14.7862945613		14.7862945613		11.829035649		2.9572589123								59.1451782452

		Install 3										4.5949354982		18.3797419928		22.974677491		22.974677491		18.3797419928		4.5949354982						91.898709964				Install 3										7.9224859888		31.6899439552		39.6124299441		39.6124299441		31.6899439552		7.9224859888						158.4497197762				Install 3										3.0069431879		12.0277727518		15.0347159397		15.0347159397		12.0277727518		3.0069431879						60.1388637589

		Install 4												4.6702147038		18.6808588151		23.3510735189		23.3510735189		18.6808588151		4.6702147038				93.4042940757				Install 4												8.0730444		32.2921775999		40.3652219999		40.3652219999		32.2921775999		8.0730444				161.4608879997				Install 4												3.0566274636		12.2265098545		15.2831373182		15.2831373182		12.2265098545		3.0566274636				61.1325492727

		Install 5														4.7454939094		18.9819756375		23.7274695469		23.7274695469		18.9819756375		4.7454939094		94.9098781874				Install 5														8.2236028112		32.8944112446		41.1180140558		41.1180140558		32.8944112446		8.2236028112		164.4720562231				Install 5														3.1063117393		12.4252469573		15.5315586966		15.5315586966		12.4252469573		3.1063117393		62.1262347864

		Install 6																4.7158662353		14.147598706		23.5793311767		23.5793311767		18.8634649414		84.8855922361				Install 6																8.2370346479		24.7111039436		41.1851732393		41.1851732393		32.9481385914		148.2666236614				Install 6																3.08823224		9.2646967201		15.4411612002		15.4411612002		12.3529289601		55.5881803206

		Install 7																		4.7868280208		14.3604840624		23.934140104		23.934140104		67.0155922913				Install 7																		8.3789582188		25.1368746564		41.894791094		41.894791094		117.3054150632				Install 7																		3.1350670184		9.4052010553		15.6753350922		15.6753350922		43.8909382582

		Install 8																				4.8577898063		14.5733694188		24.2889490314		43.7201082565				Install 8																				8.5208817897		25.5626453692		42.6044089487		76.6879361076				Install 8																				3.1819017969		9.5457053906		15.9095089843		28.6371161717

		Install 9																						8.0622756821		24.1868270463		32.2491027285				Install 9																						11.796329451		35.3889883531		47.1853178042				Install 9																						5.8608968112		17.5826904335		23.4435872447

		Install 10																								8.2041992531		8.2041992531				Install 10																								12.0092148075		12.0092148075				Install 10																								5.9673394894		5.9673394894

						48.888		73.332		371.1796562926		511.5535606687		534.5282381597		680.0993116786		332.5422180532		211.132368078		89.8008689056		93.801306723		104.2230742856		3002.1926028449								60.018		90.027		457.9069275776		639.1901962994		678.8026262434		869.2128482433		452.286808147		304.0801697509		156.1756073299		161.4063947981		173.0691446058		3982.1577229956								31.5		47.25		239.2072589123		329.835978837		344.8706947767		438.9038320949		215.1603681042		136.9494914173		58.7932757914		62.004972915		70.5941146988		1943.5699875476





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		85%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																above (cols. N,O): total MW if elec limited, with 250 MW or 18 MW units																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"





tab44

		

						Estimated Economic Cogeneration Installed Annually

						Large and Medium Scale Applications

						Base Case

								MW Installed in Year

																														Cumulative

										2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential				73		493		634		657		558		210		89		90		94		104		3002





tab 47

		

						Estimated Economic Cogeneration Installed Annually

						High and Low Cases

								MW Installed in Year

						HIGH CASE (Low gas prices)																						Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		90		458		639		679		869		452		304		156		161		173		3982

						Small		65		71.5		78		84.5		100		133		132		137		158		177		1136

						TOTAL		155		529		717		763		969		585		436		293		319		350		5118

						LOW CASE High gas prices)

						Large/Medium		47		239		330		345		439		215		137		59		62		71		1944

						Small		34		37		40		44		48		51		65		75		90		105		588

						TOTAL		81		276		370		388		487		266		202		134		152		176		2532





tab46

		

						Estimated Economic Cogeneration Installed Annually

						Base Case

								MW Installed in Year

																												Cumulative

						Scale		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		73		493		634		657		558		210		89		90		94		104		3002

						Small		50		55		60		65		72		88		119		122		123		125		879

						TOTAL		123		548		694		722		630		298		208		212		217		229		3881





tab45

								MW

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

						Estimated Economic Cogeneration Installed Annually

						Small Scale Applications

						Base Case

								MW Installed in Year

																												Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential		50		55		60		65		72		88		119		122		123		125		879





tab42

		

				Economic Potential

				Large and Medium Scale

				Returns at $50 per MWh.

				Type of Unit				Rated Output				IRR

								(MW)				(%)

				Cogeneration

						Gas Turbine		CCC		250		25.47

								SCC		250		43.57

								CCC		150		18.62

								CCC		100		N/A

								CCC		50		N/A

								SCC		40		N/A

								SCC		26		N/A

								SCC		10		N/A

				IRR = Internal Rate of Return

				IRR computed with electricity rate

						at 50.00 Cdn$/MWh





tab32_5

		

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		2537		13750

				2005		11966		31.06				2005		11966		2483		14449

				2010		12676		33.09				2010		12676		2461		15138

				2015		13371		34.96				2015		13371		2448		15819

				2020		14037		36.44				2020		14037		2477		16514





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible






_1028446823.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

								Cost

				Type		Size				($/MWh)

						(MW)		2000		2005		2010

				CCC		250		47.24		45.79		44.34

				CCC		50		74.61		73.06		71.51





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls						Capacity Factor						90%

		(2) With fixed O&M converted						Gas Price						5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems						Boiler Efficiency						85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines								Exchange Rate Conversion						1.5		CD$/US$





tab25

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300		77.43		74.18		69.34

				Reciprocating engines		2500		59.81		57.01		52.58

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





lgcalc

		

								MW

		Small				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

		Large

		AGRA Monenco est				2328

		Plus 5%				2444.4		122.22		488.88		611.1		611.1		488.88		122.22										2444.4

		yearly shares						0.05		0.2		0.25		0.25		0.2		0.05										1

		Total potential				11214		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676

		Analytical estimate

		Potential % total				0.2179851087		0.225		0.23		0.235		0.24		0.25		0.26		0.27		0.28		0.29		0.3

		Penetration curve						5		8		15		15		11		10		9		8		8		8		97

		cogeneration installed						128		212		411		425		329		315		298		278		291		304		2990.4633105548

		Market timing - small : from Steve Williams

		%accessible						0.016		0.0301		0.046		0.0588		0.0572		0.055		0.0522		0.0464		0.0464		0.0464

		%exposed						4		7		10		12		11		10		9		8		8		8		87

		%targetable						40		43		46		49		52		55		58		58		58		58

		Market timing - large

		%accessible						2.5%		4.1%		6.2%		8.3%		6.3%		5.4%		5.0%		5.1%		5.3%		5.4%

		%exposed						5		8		12		15		11		9		8		8		8		8		92

		%targetable						50		51		52		55		57		60		62		64		66		68

		%success						0.4		0.4		0.4		0.45		0.45		0.45		0.5		0.5		0.5		0.55

								113.6416843299		187.9203420968		291.1655199732		438.6631961191		337.6320346218		294.2323132615		303.8061806452		317.239623437		330.9001439422		379.2665163771		2994.4675548038

																																				2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL								2000		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895						total potential				11213.6100218196		11364.1684329918		11514.7268441641		11665.2852553363		11815.8436665086		11966.4020776809		12108.3256486226		12250.2492195643		12392.172790506		12534.0963614478		12676.0199323895

		AGRA Monenco pot				2328																										AGRA Monenco pot				2858																										AGRA Monenco pot				1500

		plus 5%				2444.4																										plus 5%				3000.9																										plus 5%				1575

		Potential % total				0.2179851087		0.2179851087		0.2229851087		0.2279851087		0.2329851087		0.2379851087		0.2429851087		0.2479851087		0.2529851087		0.2629851087		0.2729851087						Potential % total				0.2676123027		0.2676123027		0.2776123027		0.2876123027		0.2976123027		0.3076123027		0.3176123027		0.3276123027		0.3376123027		0.3526123027		0.3676123027						Potential % total				0.1404543226		0.1404543226		0.1437543226		0.1470543226		0.1503543226		0.1536543226		0.1569543226		0.1602543226		0.1635543226		0.1710543226		0.1785543226

		Potential						2477.2194916315		2567.6126174837		2659.5113274477		2752.9156215234		2847.8254997109		2942.1428244176		3037.8793848338		3135.0351809594		3296.2806946017		3460.3646796628		3002.1926028449				Potential						3041.1912831111		3196.6298346639		3355.0795544401		3516.5404424397		3681.0124986628		3845.75319162		4013.3323559959		4183.7499917907		4419.6765808115		4659.8608769606		3982.1577229956				Potential						1596.1465796594		1655.2917579046		1715.4306216635		1776.5631709362		1838.6894057226		1900.4540505232		1963.155390892		2026.7934268291		2144.0113630524		2263.3581528399		1943.5699875476

		Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99				Penetration curve						4		6		20		13		10		15		10		8		7		6		99

		cogeneration installed - one curve						99		154		532		358		285		441		304		251		231		208		2861.9830889976				cogeneration installed - one curve						122		192		671		457		368		577		401		335		309		280		3711.578086636				cogeneration installed - one curve						64		99		343		231		184		285		196		162		150		136		1850.4810511854

		diff								90.3931258523		91.898709964		93.4042940757		94.9098781874		94.3173247068		95.7365604162		97.1557961256		161.2455136423		164.0839850611		983.1451880314				diff								155.4385515528		158.4497197762		161.4608879997		164.4720562231		164.7406929571		167.5791643759		170.4176357948		235.9265890208		240.1842961491		1618.6695938495				diff								59.1451782452		60.1388637589		61.1325492727		62.1262347864		61.7646448006		62.7013403688		63.638035937		117.2179362233		119.3467897875		667.2115731804

								2444.4																				2444.4										3000.9																				3000.9										1575																				1575

		Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100				Penetration curve 1				2		3		15		20		20		25		10		5								100

		Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100				Penetration curve 2								5		20		25		25		20		5								100

		Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100				Penetration curve 3										5		20		25		25		20		5						100

		Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100				Penetration curve 4												5		20		25		25		20		5				100

		Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100				Penetration curve 5														5		20		25		25		20		5		100

		Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90				Penetration curve 6																5		15		25		25		20		90

		Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70				Penetration curve 7																		5		15		25		25		70

		Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45				Penetration curve 8																				5		15		25		45

		Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20				Penetration curve 9																						5		15		20

		Penetration curve 10																								5						Penetration curve 10																								5						Penetration curve 10																								5

		Install 1				48.888		73.332		366.66		488.88		488.88		611.1		244.44		122.22								2444.4				Install 1				60.018		90.027		450.135		600.18		600.18		750.225		300.09		150.045								3000.9				Install 1				31.5		47.25		236.25		315		315		393.75		157.5		78.75								1575

		Install 2								4.5196562926		18.0786251705		22.5982814631		22.5982814631		18.0786251705		4.5196562926								90.3931258523				Install 2								7.7719275776		31.0877103106		38.8596378882		38.8596378882		31.0877103106		7.7719275776								155.4385515528				Install 2								2.9572589123		11.829035649		14.7862945613		14.7862945613		11.829035649		2.9572589123								59.1451782452

		Install 3										4.5949354982		18.3797419928		22.974677491		22.974677491		18.3797419928		4.5949354982						91.898709964				Install 3										7.9224859888		31.6899439552		39.6124299441		39.6124299441		31.6899439552		7.9224859888						158.4497197762				Install 3										3.0069431879		12.0277727518		15.0347159397		15.0347159397		12.0277727518		3.0069431879						60.1388637589

		Install 4												4.6702147038		18.6808588151		23.3510735189		23.3510735189		18.6808588151		4.6702147038				93.4042940757				Install 4												8.0730444		32.2921775999		40.3652219999		40.3652219999		32.2921775999		8.0730444				161.4608879997				Install 4												3.0566274636		12.2265098545		15.2831373182		15.2831373182		12.2265098545		3.0566274636				61.1325492727

		Install 5														4.7454939094		18.9819756375		23.7274695469		23.7274695469		18.9819756375		4.7454939094		94.9098781874				Install 5														8.2236028112		32.8944112446		41.1180140558		41.1180140558		32.8944112446		8.2236028112		164.4720562231				Install 5														3.1063117393		12.4252469573		15.5315586966		15.5315586966		12.4252469573		3.1063117393		62.1262347864

		Install 6																4.7158662353		14.147598706		23.5793311767		23.5793311767		18.8634649414		84.8855922361				Install 6																8.2370346479		24.7111039436		41.1851732393		41.1851732393		32.9481385914		148.2666236614				Install 6																3.08823224		9.2646967201		15.4411612002		15.4411612002		12.3529289601		55.5881803206

		Install 7																		4.7868280208		14.3604840624		23.934140104		23.934140104		67.0155922913				Install 7																		8.3789582188		25.1368746564		41.894791094		41.894791094		117.3054150632				Install 7																		3.1350670184		9.4052010553		15.6753350922		15.6753350922		43.8909382582

		Install 8																				4.8577898063		14.5733694188		24.2889490314		43.7201082565				Install 8																				8.5208817897		25.5626453692		42.6044089487		76.6879361076				Install 8																				3.1819017969		9.5457053906		15.9095089843		28.6371161717

		Install 9																						8.0622756821		24.1868270463		32.2491027285				Install 9																						11.796329451		35.3889883531		47.1853178042				Install 9																						5.8608968112		17.5826904335		23.4435872447

		Install 10																								8.2041992531		8.2041992531				Install 10																								12.0092148075		12.0092148075				Install 10																								5.9673394894		5.9673394894

						48.888		73.332		371.1796562926		511.5535606687		534.5282381597		680.0993116786		332.5422180532		211.132368078		89.8008689056		93.801306723		104.2230742856		3002.1926028449								60.018		90.027		457.9069275776		639.1901962994		678.8026262434		869.2128482433		452.286808147		304.0801697509		156.1756073299		161.4063947981		173.0691446058		3982.1577229956								31.5		47.25		239.2072589123		329.835978837		344.8706947767		438.9038320949		215.1603681042		136.9494914173		58.7932757914		62.004972915		70.5941146988		1943.5699875476





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		85%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																above (cols. N,O): total MW if elec limited, with 250 MW or 18 MW units																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"





tab44

		

						Estimated Economic Cogeneration Installed Annually

						Large and Medium Scale Applications

						Base Case

								MW Installed in Year

																														Cumulative

										2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential				73		493		634		657		558		210		89		90		94		104		3002





tab 47

		

						Estimated Economic Cogeneration Installed Annually

						High and Low Cases

								MW Installed in Year

						HIGH CASE (Low gas prices)																						Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		90		458		639		679		869		452		304		156		161		173		3982

						Small		65		71.5		78		84.5		100		133		132		137		158		177		1136

						TOTAL		155		529		717		763		969		585		436		293		319		350		5118

						LOW CASE High gas prices)

						Large/Medium		47		239		330		345		439		215		137		59		62		71		1944

						Small		34		37		40		44		48		51		65		75		90		105		588

						TOTAL		81		276		370		388		487		266		202		134		152		176		2532





tab46

		

						Estimated Economic Cogeneration Installed Annually

						Base Case

								MW Installed in Year

																												Cumulative

						Scale		2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Large/Medium		73		493		634		657		558		210		89		90		94		104		3002

						Small		50		55		60		65		72		88		119		122		123		125		879

						TOTAL		123		548		694		722		630		298		208		212		217		229		3881





tab45

								MW

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		TOTAL

		Adopted case						50		55		60		65		72		88		119		122		123		125		879

						Estimated Economic Cogeneration Installed Annually

						Small Scale Applications

						Base Case

								MW Installed in Year

																												Cumulative

								2001		2002		2003		2004		2005		2006		2007		2008		2009		2010		Total

						Potential		50		55		60		65		72		88		119		122		123		125		879





tab42

		

				Economic Potential

				Large and Medium Scale

				Returns at $50 per MWh.

				Type of Unit				Rated Output				IRR

								(MW)				(%)

				Cogeneration

						Gas Turbine		CCC		250		25.47

								SCC		250		43.57

								CCC		150		18.62

								CCC		100		N/A

								CCC		50		N/A

								SCC		40		N/A

								SCC		26		N/A

								SCC		10		N/A

				IRR = Internal Rate of Return

				IRR computed with electricity rate

						at 50.00 Cdn$/MWh





tab32_5

		

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		2537		13750

				2005		11966		31.06				2005		11966		2483		14449

				2010		12676		33.09				2010		12676		2461		15138

				2015		13371		34.96				2015		13371		2448		15819

				2020		14037		36.44				2020		14037		2477		16514





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible






_1016026019.xls
Cogen List

		Table 3.1

		Industrial Cogeneration Potential In Ontario

				February 2000

		Project Location		Market Segment		Electrical Capacity (MW)		Probability of Proceeding

		Identified 10-40 MW

		GTA		nug		10		H

		N. Ont.		ind		20		M

		Central Ont.		nug		20		M

		GTA		inst		15		M

		GTA		nug		20		M

		GTA		ind		11		M

		GTA		nug		25		M

		Totals		10		121

		Identified 40-100 MW

		GTA		ind		40		M

		East. Ont.		ind		40		M

		East. Ont.		nug		50		M

		GTA		nug		50		M

		GTA		ind		40		M

		East. Ont.		nug		90		L

		NW Ont. Pulp & Paper		nug		65		M				65

		Totals		8		375

		Identified 100-250 MW

		Ottawa/Carlton Pulp & Paper		nug		153		L				153

		East Ont.		ind		110		M

		GTA		nug		150		M

		GTA		nug		100		M

		East. Ont. Pulp & Paper		nug		180		M				180

		N. Ont.		nug		120		L

		GTA		nug		100		L

		GTA		nug		100		L

		NW Ont. Pulp & Paper		nug		165		L				165

		NW Ont.Pulp & Paper		nug		180		L				180

		Totals		10		1,358

		Idebtified :250 MW  and larger

		GTA Pulp & paper		ind		250		H				250

		Niag. Penn Pulp & Paper		ind		350		M				350

		West. Ont.		nug		550		H				1343

		Niag. Penn.		nug		350		M

		Totals		4		1,500

		Total		32		3,354

		Plus 20% unidentified				688

		Total potential				4,146

		Notes:

		List of all cogeneration projects identified from data sources

		Market segment includes industrial, commercial, institutional and institutional

		Segment listed as NUG if project proposed by non utility generator

		Project capacity refers to proposed size.

		Projects not necessarily sized by embedded electrical or thermal loads

		Probability of proceeding refers to opinion of data source at the time project identified,

		does not necessarily refer to economic viability

		Additional technical potential of 20% based on subjective estimate





LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Class 43		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible





table 43

		Table 4.3

		Industrial Cogeneration Potential In Ontario

		Economic Potential at $50/MWh Electricity Price

		Project Location		Market Segment		Electrical Capacity (MW)		Probability of Proceeding

		Identified 100-250 MW

		Ottawa/Carlton Pulp & Paper		nug		153		L

		GTA		nug		150		M

		East. Ont. Pulp & Paper		nug		180		M

		NW Ont. Pulp & Paper		nug		165		L

		NW Ont.Pulp & Paper		nug		180		L

		Totals		5		828

		Identified :250 MW  and larger

		GTA Pulp & paper		ind		250		H

		Niag. Penn Pulp & Paper		ind		350		M

		West. Ont.		nug		550		H

		Niag. Penn.		nug		350		M

		Totals		4		1,500

		Total economic potential				2,328

		Notes:

		List of all cogeneration projects identified from data sources

		Market segment includes industrial, commercial, institutional and institutional

		Segment listed as NUG if project proposed by non utility generator

		Project capacity refers to proposed size.

		Projects not necessarily sized by embedded electrical or thermal loads

		Probability of proceeding refers to opinion of data source at the time project identified,

		does not necessarily refer to economic viability

		Additional technical potential of 20% based on subjective estimate






_1022674210.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls						Capacity Factor						90%

		(2) With fixed O&M converted						Gas Price						5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems						Boiler Efficiency						85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines								Exchange Rate Conversion						1.5		CD$/US$





tab26

		

				Table 2-6

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300

				Reciprocating engines		2500

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(MW)

				CCC		250		47.24

				SCC		250		42.78

				CCC		100		57.52

				CCC		50		74.61

				SCC		10		72.99





tab32_5

		

				Table 3-2								Table 3-5

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		1472		12685

				2005		11966		31.06				2005		11966		1610		13577

				2010		12676		33.09				2010		12676		1773		14449

				2015		13371		34.96				2015		13371		1960		15331

				2020		14037		36.44				2020		14037		2171		16208





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts

0

0

0

0

0

0

0

0

0

0

0

0



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"






_1022676065.xls
prices

		

										Price

								Year		($/kWh)

								2001		0.038

								2002		0.038

								2003		0.038

								2004		0.038

								2004		0.038

								2005		0.0369284678

								2006		0.0377558473

								2007		0.0385832268

								2008		0.0394106063

								2009		0.0412027431

								2010		0.0429948799

								2011		0.0448937369

								2012		0.0467925939

								2013		0.0467925939

								2014		0.0467925939

								2015		0.0467925939

								2016		0.0467925939

								2017		0.0467925939

								2018		0.0467925939

								2019		0.0467925939

								2020		0.0467925939





Tab23

		Indicative Performance Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Assumed												Total

								Capacity						Electric-to		Output		Output		Conversion		Total		Total

		Size		Technology		Fuel		Factor		Heat Rate		Heat Rate		Thermal (E/T)		Electricity		Thermal		Efficiency		Heat		Electricity

		(kW)						(%)		(Btu/kWh)		(GJ/kWh)		Ratio		(GJ/h)		(GJ/h)		(%)		(Annual GJ)		(Annual GJ)

		75		microturbine		gas		90%		12,186		0.013		0.6		0.27		0.45		75%		3,548		2,129

		100		microturbine		gas		90%		11,373		0.012		0.6		0.36		0.60		80%		4,730		2,838

				Fuel cells:

		200		Phosphoric Acid		gas		90%		8,530		0.009		1.3		0.72		0.55		71%		4,367		5,676

		300		Solid Oxide-Atmospheric		gas		90%		7,582		0.008		1.5		1.08		0.72		75%		5,676		8,515

		600		Solid Oxide-Atmospheric		gas		90%		7,417		0.008		1.6		2.16		1.35		75%		10,643		17,029

		450		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		1.62		0.81		75%		6,386		12,772

		900		Solid Oxide-Atmos. Hybrid		gas		90%		6,824		0.007		2.0		3.24		1.62		75%		12,772		25,544

		220		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		0.79		0.20		75%		1,561		6,244

		920		Solid Oxide-Press. Hybrid		gas		90%		5,687		0.006		4.0		3.31		0.83		75%		6,528		26,112

		300		Molten Carbonate		gas		90%		7,000		0.007		2.0		1.08		0.54		73%		4,257		8,515

		1200		Molten Carbonate		gas		90%		6,700		0.007		2.0		4.32		2.16		76%		17,029		34,059

		250		PEM		gas		90%		8,530		0.009		1.2		0.90		0.75		73%		5,913		7,096

		300		Reciprocating engines		gas		90%		9,222		0.010		0.8		1.08		1.35		83%		10,643		8,515

		1000		Reciprocating engines		gas		90%		8,124		0.009		1.0		3.60		3.60		84%		28,382		28,382

		2500		Reciprocating engines		gas		90%		7,935		0.008		1.1		9.00		8.18		82%		64,505		70,956

		5000		Reciprocating engines		diesel		90%		7,417		0.008		1.2		18.00		15.00		84%		118,260		141,912

		1500		Aeroderivative turbines		gas		90%		12,186		0.013		0.5		5.40		10.80		84%		85,147		42,574

		3000		Aeroderivative turbines		gas		90%		10,339		0.011		0.6		10.80		18.00		88%		141,912		85,147

		6000		Aeroderivative turbines		gas		90%		9,749		0.010		0.6		21.60		36.00		93%		283,824		170,294





Tab24

		Indicative Cost Attributes of Small Cogeneration Systems

		(Estimated Data for 2001) ($ figures in CD$ except where noted)

								Installed		Installed

								Capital		Capital		O&M		O&M		Fuel										Thermal		Adjusted

		Size		Technology		Fuel		Cost		Cost		Cost		Cost		Cost		Heat Rate		Availability		Taxes		LUEC		Credit		LUEC

		(kW)						(US$/kW) (1)		($/kW) (1)		(US$/MWh) (2)		($/MWh) (2)		($/MWh)		(Btu/kWh)		(%)				($/MWh)		($/MWh)(3)		($/MWh)

		75		Microturbine		gas		1050		1575		12.28		18.42		68.55		12,186		92%				115.51		37.64		77.87

		100		Microturbine		gas		900		1350		10.03		15.04		63.97		11,373		92%				103.48		37.64		65.84

				Fuel cells:

		200		Phosphoric Acid		gas		2000		3000		11.76		17.64		47.98		8,530		98%				119.98		17.37		102.61

		300		Solid Oxide-Atmospheric		gas		2100		3150		5.96		8.94		42.65		7,582		96%				108.67		15.05		93.61

		600		Solid Oxide-Atmospheric		gas		1900		2850		3.89		5.84		41.72		7,417		95%				99.20		14.11		85.09

		450		Solid Oxide-Atmos. Hybrid		gas		1600		2400		8.95		13.43		38.39		6,824		93%				95.30		11.29		84.01

		900		Solid Oxide-Atmos. Hybrid		gas		1500		2250		8.95		13.43		38.39		6,824		93%				92.59		11.29		81.30

		220		Solid Oxide-Press. Hybrid		gas		1800		2700		11.45		17.17		31.99		5,687		92%				98.08		5.65		92.44

		920		Solid Oxide-Press. Hybrid		gas		1500		2250		5.54		8.31		31.99		5,687		92%				81.06		5.65		75.42

		300		Molten Carbonate		gas		2000		3000		12.26		18.39		39.38		7,000		92%				112.12		11.29		100.83

		1200		Molten Carbonate		gas		1900		2850		8.90		13.34		37.69		6,700		92%				102.67		11.29		91.38

		250		PEM		gas		2000		3000		9.07		13.61		47.98		8,530		93%				115.95		18.82		97.13

		300		Reciprocating engines		gas		1100		1650		15.92		23.89		51.87		9,222		92%				105.66		28.23		77.43

		1000		Reciprocating engines		gas		975		1463		9.91		14.86		45.70		8,124		92%				87.06		22.58		64.48

		2500		Reciprocating engines		gas		900		1350		7.50		11.25		44.63		7,935		92%				80.34		20.53		59.81

		5000		Reciprocating engines		diesel		600		900		13.39		20.08		66.75		7,417		95%				103.14		30.11		73.03

		1500		Aeroderivative turbines		gas		1467		2200		7.04		10.57		68.55		12,186		92%				118.98		45.16		73.81

		3000		Aeroderivative turbines		gas		1267		1900		5.37		8.05		58.16		10,339		92%				100.64		37.64		63.00

		6000		Aeroderivative turbines		gas		1233		1850		5.00		7.50		54.838		9,749		92%				95.854		37.64		58.22

		(1) Including gas compression				Assumptions

		and moderate emission controls						Capacity Factor						90%

		(2) With fixed O&M converted						Gas Price						5.625		$/MMBtu		Diesel Price		9		$/MMBtu

		at assumed capacity factor												5.33		$/GJ				8.53		$/GJ

		(3) Most small cogen systems						Boiler Efficiency						85%				Capital Recovery		7		years

		limited to lower temperature

		applications -- exception small gas turbines								Exchange Rate Conversion						1.5		CD$/US$





tab26

		

				Small

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(kW)

				Microturbine		100		65.84		55.04		51.02

				Solid Oxide-Atmospheric fuel cell		600		85.09		72.36		67.97

				Solid Oxide-Press. Hybrid fuel cell		920		75.42		67.68		60.15

				Reciprocating engines		300

				Reciprocating engines		2500

				Aeroderivative turbines		1500		73.81		66.50		59.37

				Aeroderivative turbines		3000		63.00		56.03		49.34

				Aeroderivative turbines		6000		58.22		49.49		46.41





tab22

		

				Large and Medium

				Cogeneration Technologies

				LUEC Cost Forecast

										Cost

										($/MWh)

				Type		Size		2000		2005		2010

						(MW)

				CCC		250		47.24

				SCC		250		42.78

				CCC		100		57.52

				CCC		50		74.61

				SCC		10		72.99





tab32_5

		

												Table 3-5

				INDUSTRIAL COGENERATION								TOTAL COGENERATION

				POTENTIAL IN ONTARIO								POTENTIAL IN ONTARIO

				Analytical Method

														MW

						MW		TWh.						Industrial		Commercial		Total

				2000		11214		28.43				2000		11214		1472		12685

				2005		11966		31.06				2005		11966		1610		13577

				2010		12676		33.09				2010		12676		1773		14449

				2015		13371		34.96				2015		13371		1960		15331

				2020		14037		36.44				2020		14037		2171		16208





pricetab

		

						Forecast of

						Electricity Prices in

						Ontario

						Annual Averages

										Price

						Year				($/kWh)

						2001				0.038

						2005				0.037

						2010				0.043

						2015				0.047

						2020				0.047





capcosts

		

		Capital costs for awarded projects

		Source: Presentation by John Alsip, Regional Sales Director, Rolls Royce Energy Systems

		Date		Size (MW)		Cost US$M)		Cost/kW				Size (MW)		Cost/kW

		Jan-99		1000		350		350.0				1000		350.0

		Nov-98		775		300		387.1				775		387.1

		Nov-98		122		50		409.8				122		409.8

		Apr-98		400		170		425.0				400		425.0

		Jul-98		480		250		520.8				480		520.8

		Apr-98		540		300		555.6				540		555.6

		Jan-99		485		300		618.6				485		618.6

		Apr-98		450		280		622.2				450		622.2

		Jan-98		250		160		640.0				250		640.0

		Mar-98		270		190		703.7				270		703.7

		May-99		450		320		711.1				450		711.1

		Apr-98		400		320		800.0				400		800.0





capcosts

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0

		0



Cost/kW

size (MW)

cost/kW

Costs for Awarded Contracts

0

0

0

0

0

0

0

0

0

0

0

0



LUEC Table

		

		Cogeneration Potential in Ontario

		Estimated Total Costs of Electricity Generated

		Base Case Gas Prices

		Type of Unit				Rated Output		Fuel				Levelized		Levelized		Plant		Thermal Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

												O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)				(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

		Gas Turbine Plants				CCC 250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC 250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC 150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC 100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC 50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC 40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC 26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC 10		Gas		1,600		22.50		62.50		11,124		4,780		93.0%		4.37		116.05		39.35		78.50

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*								SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*								SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*								SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*								SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible





tab33

		

				Data for Estimation of Technical Cogeneration Potential

				Commercial Sector

				Ontario

						Historical Data										Assumptions

										Average Annual						Average Annual				Fraction of

						Energy Use 1997				Growth Rate						Growth Rate				Electricity

		Sector				Electricity		Heat		1981-97						2000-20				in Large

						PJ		PJ		Electricity		Heat				Electricity		Heat		Buildings

		Offices				46.34		52.44		4.35%		1.14%				2.60%		1.07%		46%

		Health				9.78		41.79		0.28%		-2.50%				0.11%		-1.87%		40%

		Schools				9.31		34.91		0.36%		-2.64%				0.37%		-2.00%		27%

		Hotels				14.82		12.04		1.50%		0.65%				0.33%		0.43%		10%

		Retail				55.05		33.16		1.74%		-0.89%				0.43%		-0.50%		10%

		Other				20.26		35.29		1.99%		-1.35%				1.09%		-0.50%		5%

						Data Source:  Office of Energy Efficiency, NRCan





tab34

		

				Table 3.4

				Estimated Technical Cogeneration Potential

				Commercial Sector

				Ontario

		Sector				2000		2005		2010		2015		2020

						MW

		Offices				1144		1227		1308		1389		1467

		Health				857		755		683		617		572

		Schools				241		212		192		174		161

		Hotels				55		55		56		57		60

		Retail				148		144		137		131		134

		Other				92		90		85		81		83

		Totals				2537		2483		2461		2448		2477





indcgn

		

		Industrial energy demand																																		potential

						NRCan 2020																				OEE										cogeneration						cogeneration

								PJ										ind		ind						ind		elec								inds: elec demand						inds: gas demand				Boiler

								non-combust Canada		non-combust		Net		% energy		% elec		electricity		electricity		% elec				energy		Ontario								Ontario						Ontario				Efficiency

				Total  Ontario		total Canada		Canada		Ontario		Ontario		growth		ind		Canada		Ontario		growth				Ontario		PJ		TWh						PJ		TWh				PJ		PJ cogen		%

		1985																								913.457999		157.266002		43.6853500356						95.09925125		26.4166700122				180.0650015		90.03250075		76.5276256375

		1990		1098.1		3122.2		638.3		224.4946608161		873.6053391839						595.2		209.3360835308						873.77701		164.303998		45.6403645644						96.42274825		26.7843110089				195.192004		97.596002		82.9566017

		1995		1123.8		3424.7		728.9		239.1852775426		884.6147224574		0.25%		24.58%		662.7		217.4620433907		0.76%				865.264991		156.961999		43.6009040822						97.36999975		27.0474385306				197.923		98.9615		84.117275

		2000		1196.3		3690.5		826.3		267.850613738		928.449386262		1.00%		24.13%		691.1		224.0246389378		1.00%				909.4022015407		164.9686384328		45.8249883839						102.3368483155		28.4271297251				208.0190621459		104.009531073		88.408101412

		2005		1271.6		3967.1		876.1		280.8219505432		990.7780494568		1.31%		24.71%		763.7		244.7936578357		1.79%				970.4521891513		180.2626560257		50.0733605908						111.8243580229		31.0625701716				221.983797601		110.9918988005		94.3431139804

		2010		1345.2		4220.3		927.6		295.6679667322		1049.5320332678		1.16%		24.84%		818		260.7335023577		1.27%				1028.0008321012		192.0005365557		53.3339090444						119.1058492854		33.0852228145				235.1476262281		117.5738131141		99.937741147

		2015		1410.8		4480.1		964.5		303.7246043615		1107.0753956385		1.07%		24.89%		875		275.5407245374		1.11%				1084.363689569		202.9043696945		56.3627758137						125.8699465622		34.9641537561				248.0402151513		124.0201075757		105.4170914393

		2020		1474.8		4716.1		999.7		312.6222005471		1162.1777994529		0.98%		24.71%		918.3		287.1671168974		0.83%				1138.3356648651		211.4658838503		58.7409932159						131.1810067967		36.439460068				260.3859073701		130.192953685		110.6640106323

																																						cogeneration potential share of gas						0.5		0.85

						1 PJ= 2.7778x10^8 Kwh																		capacity  MW				250		18		capacity  GJ/hr				1629		18						Plant		Class 43		Thermal		E/T ratio		Thermal

						1PJ = 277.78 MWh.																		capacity factor				0.9		0.93		capacity factor				0.9		0.5								Heat Rate		Output				Output

						277.78																		elec output (Mwh)				1971000		146642.4		yr heat output (GJ)				12843036		78840						(Btu/kWh)		(Btu/kWh)		(Btu/kWh)				MJ/kWh		GJ/hour

																								Total MW		1990		3397		3287.7094084653		MW if heat limited				10522.146334348

																										1995		3431		3320.0076754744						10669				CCC		250		6,705		< 6,000

																										2000		3606		3489.3614333328						11214				SCC		250		10,506		4,330		6,176		0.7011010363		6.5162976		1629.0744

																										2005		3940		3812.8553753119						11966				CCC		150		7,715		< 6,000

																										2010		4197		4061.1310961966						12676				CCC		100		7,519		< 6,000

																										2015		4435		4291.7653257785						13371				CCC		50		7,262		< 6,001

				Data sources: NRCan is NRCan 2020																						2020		4622		4472.8556080897						14037				SCC		40		8,652		4,350		4,302		1.0111576011		4.5390402		181.561608

				OEE is spreadsheet "Ontario ind", historical data obtained from Office of Energy Efficiency																																				SCC		26		10,815		4,840		5,975		0.810041841		6.3042225		163.909785

						Total is total electricity demand from OEE data.																																		SCC		10		11,124		4,780		6,344		0.7534678436		6.6935544		66.935544

						"Potential cogeneration inds" is total of electricity in pulp and paper, smelting and refining, pete refining, chemicals, iron and

								steel, plus 25% of "other"






_1022669625.xls
tolls

		

						DISTRIBUTION AND TRANSMISSION CHARGES

						(All prices in $2000/Mcf)

										Distribution Tariffs for Cogeneration

						Transmission				>50 MW				10 MW				<500 kW

		YEAR				Tolls				Sudbury		Toronto		Sudbury		Toronto		Sudbury		Toronto

		2000				0.98				0.4		0.4		0.8		0.8		2.5		2.75

		2001				0.97				0.4		0.4		0.8		0.8		2.44		2.69

		2002				0.95				0.4		0.4		0.8		0.8		2.39		2.63

		2003				0.94				0.4		0.4		0.8		0.8		2.34		2.57

		2004				0.93				0.4		0.4		0.8		0.8		2.29		2.52

		2005				0.91				0.4		0.4		0.8		0.8		2.24		2.46

		2006				0.90				0.4		0.4		0.8		0.8		2.19		2.41

		2007				0.89				0.4		0.4		0.8		0.8		2.14		2.35

		2008				0.87				0.4		0.4		0.8		0.8		2.09		2.30

		2009				0.86				0.4		0.4		0.8		0.8		2.05		2.25

		2010				0.85				0.4		0.4		0.8		0.8		2.00		2.20

		2011				0.84				0.4		0.4		0.8		0.8		1.97		2.17

		2012				0.83				0.4		0.4		0.8		0.8		1.94		2.13

		2013				0.82				0.4		0.4		0.8		0.8		1.91		2.10

		2014				0.82				0.4		0.4		0.8		0.8		1.88		2.07

		2015				0.81				0.4		0.4		0.8		0.8		1.85		2.04

		2016				0.80				0.4		0.4		0.8		0.8		1.83		2.01

		2017				0.79				0.4		0.4		0.8		0.8		1.80		1.98

		2018				0.78				0.4		0.4		0.8		0.8		1.77		1.95

		2019				0.78				0.4		0.4		0.8		0.8		1.75		1.92

		2020				0.77				0.4		0.4		0.8		0.8		1.72		1.89





gas prices

		

								Table 2-1

						FORECAST GAS PRICES																		FORECAST GAS PRICES

										Alberta Border														Alberta Border

						(All prices in $2000/Mcf)																		(All prices in $2000/Mcf)

						LOW CASE				BASE CASE				HIGH CASE														LOW CASE				BASE CASE				HIGH CASE

								5 yr				5 yr				5 yr														5 yr				5 yr				5 yr

		YEAR				$		AAGR		$		AAGR		$		AAGR								YEAR				$		AAGR		$		AAGR		$		AAGR

		2000				3.00				3.00				3.00										2000				3.00				3.00				3.00

		2001				2.90				3.03				3.09										2005				2.51		-3.50%		3.15		1.00%		3.49		3.10%

		2002				2.79				3.06				3.19										2010				2.10		-3.50%		3.43		1.70%		4.07		3.10%

		2003				2.70				3.09				3.29										2015				2.34		2.20%		3.86		2.40%		4.65		2.70%

		2004				2.60				3.12				3.39										2020				2.61		2.20%		4.35		2.40%		5.31		2.70%

		2005				2.51		-0.035		3.15		0.01		3.49		0.031

		2006				2.42				3.21				3.60

		2007				2.34				3.26				3.71

		2008				2.26				3.32				3.83

		2009				2.18				3.37				3.95

		2010				2.10		-0.035		3.43		0.017		4.07		0.031																				-0.0220672315		-0.0141308314		RATE OF TRANSMISSION PRICE inCREASE 2000--2010

		2011				2.15				3.51				4.18

		2012				2.19				3.60				4.29

		2013				2.24				3.68				4.41

		2014				2.29				3.77				4.53

		2015				2.34		0.022		3.86		0.024		4.65		0.027

		2016				2.39				3.95				4.78

		2017				2.45				4.05				4.91

		2018				2.50				4.15				5.04

		2019				2.56				4.25				5.17

		2020				2.61		0.022		4.35		0.024		5.31		0.027																				-0.015		-0.01		Rate of Transmission price increase 2010-2020





del price

		

						DELIVERED PRICES FOR GAS FOR COGENERATION

						LOW, BASE AND HIGH CASES

						(All prices in $2000/Mcf)

																						<500 kW

						>50 MW								10 MW										Sudbury						Toronto

		YEAR				Low		Base		High				Low		Base		High				Low		Base		High		Low		Base		High

		2000				4.38		4.38		4.38				4.78		4.78		4.78				6.48		6.48		6.48		6.73		6.73		6.73

		2001				4.26		4.40		4.46				4.66		4.80		4.86				6.31		6.44		6.50		6.55		6.69		6.75

		2002				4.15		4.41		4.54				4.55		4.81		4.94				6.14		6.40		6.53		6.38		6.64		6.77

		2003				4.03		4.43		4.63				4.43		4.83		5.03				5.97		6.37		6.56		6.21		6.60		6.80

		2004				3.93		4.45		4.72				4.33		4.85		5.12				5.81		6.33		6.60		6.04		6.56		6.83

		2005				3.82		4.47		4.81				4.22		4.87		5.21				5.66		6.30		6.64		5.88		6.53		6.87

		2006				3.72		4.51		4.90				4.12		4.91		5.30				5.51		6.29		6.69		5.73		6.51		6.91

		2007				3.62		4.55		5.00				4.02		4.95		5.40				5.36		6.29		6.74		5.58		6.50		6.95

		2008				3.53		4.59		5.10				3.93		4.99		5.50				5.22		6.28		6.80		5.43		6.49		7.00

		2009				3.44		4.64		5.21				3.84		5.04		5.61				5.08		6.28		6.86		5.29		6.48		7.06

		2010				3.35		4.68		5.32				3.75		5.08		5.72				4.95		6.28		6.92		5.15		6.48		7.12

		2011				3.39		4.75		5.42				3.79		5.15		5.82				4.96		6.32		6.99		5.16		6.52		7.19

		2012				3.43		4.83		5.53				3.83		5.23		5.93				4.97		6.37		7.07		5.16		6.56		7.26

		2013				3.47		4.91		5.63				3.87		5.31		6.03				4.98		6.42		7.15		5.17		6.61		7.34

		2014				3.51		4.99		5.75				3.91		5.39		6.15				4.99		6.47		7.23		5.18		6.66		7.42

		2015				3.55		5.07		5.86				3.95		5.47		6.26				5.01		6.52		7.31		5.19		6.71		7.50

		2016				3.59		5.16		5.98				3.99		5.56		6.38				5.02		6.58		7.40		5.20		6.76		7.59

		2017				3.64		5.24		6.10				4.04		5.64		6.50				5.04		6.64		7.50		5.22		6.82		7.68

		2018				3.68		5.33		6.22				4.08		5.73		6.62				5.06		6.70		7.59		5.23		6.88		7.77

		2019				3.73		5.42		6.35				4.13		5.82		6.75				5.08		6.77		7.70		5.25		6.94		7.87

		2020				3.78		5.52		6.48				4.18		5.92		6.88				5.10		6.84		7.80		5.27		7.01		7.97





Sheet3

		

								1995		1996		1997		1998		1999

		Average Empress (US$)						0.88		1.1		1.43		1.51		1.94				0.76								2.42

		C$/US$						0.7286		0.7334		0.7222		0.6741		0.6711				0.7286		0.7334		0.7222		0.6741		0.6711

		Average Empress (C$)						1.2077957727		1.4998636488		1.980060925		2.2400237354		2.8907763374				1.0430963492		0		0		0		3.6060199672

		% change								24.2%		32.0%		13.1%		29.1%

		NEB Price Analysis						2000		2005		2010		2015		2020		2025

		Case 1

		Alberta Border, $/GJ						1.91				1.99						2.75

		Alberta Border, $/Mcf						2.01505				2.09945						2.90125

		% growth										0.41%						2.18%

		Case 2

		Alberta Border, $/GJ						1.91				2.6						3.86

		Alberta Border, $/Mcf						2.01505				2.743						4.0723

		% growth										3.13%						2.67%

																		2.42%

								Note: NEB document says average price growth in Case 1 is 1.5%; in Case 2, 2.8%.  Assuming those rates from 2000 to 2025

								and using final values to infer backwards, Case 1 has 2000 price of about $1.89; Case 2 has a price of $1.93 ($/GJ).  The price is taken in

								the middle, under the assumption that there were rounding errors in both growth rates quoted.

		NEB Ontario price analysis

		Case 1 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		23.78		22.62		22.62		23.06		23.52

		% growth						-1.61%		-2.00%		-1.00%		0.00%		0.39%		0.40%

		gas				9.48		10.49		10.25		10.39		10.78		11.25		11.65

		% growth						2.05%		-0.46%		0.27%		0.74%		0.86%		0.70%

		commercial

		Elec				23.56		21.73		19.64		18.68		18.68		19.05		19.42

		% growth						-1.60%		-2.00%		-1.00%		0.00%		0.39%		0.39%

		gas				7.1		8.21		8.01		8.13		8.51		9.05		9.52

		% growth						2.95%		-0.49%		0.30%		0.92%		1.24%		1.02%

		industrial

		Elec				21.27		19.62		17.73		16.86		16.86		17.19		17.53

		% growth						-1.60%		-2.01%		-1.00%		0.00%		0.39%		0.39%

		gas				4.19		5.18		5.1		5.27		5.65		6.18		6.64

		% growth						4.33%		-0.31%		0.66%		1.40%		1.81%		1.45%

		Case 2 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		25.27		25.27		25.9		26.54		27.19

		% growth						-1.61%		-0.80%		0.00%		0.49%		0.49%		0.49%

		gas				9.48		10.79		10.87		11.19		11.9		12.72		13.05

		% growth						2.62%		0.15%		0.58%		1.24%		1.34%		0.51%

		commercial

		Elec				23.56		21.73		20.87		20.87		21.39		21.91		22.46

		% growth						-1.60%		-0.80%		0.00%		0.49%		0.48%		0.50%

		gas				7.1		8.58		8.75		9.03		9.71		10.49		10.77

		% growth						3.86%		0.39%		0.63%		1.46%		1.56%		0.53%

		industrial

		Elec				21.27		19.62		18.84		18.84		19.31		19.78		20.27

		% growth						-1.60%		-0.81%		0.00%		0.49%		0.48%		0.49%

		gas				4.19		5.54		5.84		6.24		6.98		7.84		8.27

		% growth						5.74%		1.06%		1.33%		2.27%		2.35%		1.07%

		EIA Price Analysis						2000		2005		2010		2015		2020		2025

		Economic Growth Case

		Well price, lower 48, $/Mcf						2.11		2.52		2.71		2.91		3.09

		Import price						2.2		2.45		2.6		2.72		2.88

		% growth (import)								2.18%		1.20%		0.91%		1.15%

		Reference Case

		Well price, lower 48, $/Mcf						2.1		2.35		2.52		2.62		2.68

		Import price						2.19		2.36		2.48		2.55		2.68

		% growth (import)								1.51%		1.00%		0.56%		1.00%

		Oil Price Case

		Well price, lower 48, $/Mcf						2.12		2.41		2.52		2.64		2.7

		Import price						2.2		2.42		2.54		2.61		2.73

		% growth (import)								1.92%		0.97%		0.55%		0.90%

								0.12178		$/M3

								28		MCF/M3

								3.40984






_1003823044.xls
tolls

		

						DISTRIBUTION AND TRANSMISSION CHARGES

						(All prices in $2000/Mcf)

										Distribution Tariffs for Cogeneration

						Transmission				>50 MW				10 MW				<500 kW

		YEAR				Tolls				Sudbury		Toronto		Sudbury		Toronto		Sudbury		Toronto

		2000				0.98				0.40		0.40		0.80		0.80		2.50		2.75

		2001				0.97				0.40		0.40		0.80		0.80		2.44		2.69

		2002				0.95				0.40		0.40		0.80		0.80		2.39		2.63

		2003				0.94				0.40		0.40		0.80		0.80		2.34		2.57

		2004				0.93				0.40		0.40		0.80		0.80		2.29		2.52

		2005				0.91				0.40		0.40		0.80		0.80		2.24		2.46

		2006				0.90				0.40		0.40		0.80		0.80		2.19		2.41

		2007				0.89				0.40		0.40		0.80		0.80		2.14		2.35

		2008				0.87				0.40		0.40		0.80		0.80		2.09		2.30

		2009				0.86				0.40		0.40		0.80		0.80		2.05		2.25

		2010				0.85				0.40		0.40		0.80		0.80		2.00		2.20

		2011				0.84				0.40		0.40		0.80		0.80		1.97		2.17

		2012				0.83				0.40		0.40		0.80		0.80		1.94		2.13

		2013				0.82				0.40		0.40		0.80		0.80		1.91		2.10

		2014				0.82				0.40		0.40		0.80		0.80		1.88		2.07

		2015				0.81				0.40		0.40		0.80		0.80		1.85		2.04

		2016				0.80				0.40		0.40		0.80		0.80		1.83		2.01

		2017				0.79				0.40		0.40		0.80		0.80		1.80		1.98

		2018				0.78				0.40		0.40		0.80		0.80		1.77		1.95

		2019				0.78				0.40		0.40		0.80		0.80		1.75		1.92

		2020				0.77				0.40		0.40		0.80		0.80		1.72		1.89





gas prices

		

						FORECAST GAS PRICES

										Alberta Border

						(All prices in $2000/Mcf)

						LOW CASE				BASE CASE				HIGH CASE

								5 yr				5 yr				5 yr

		YEAR				$		AAGR		$		AAGR		$		AAGR

		2000				3.00				3.00				3.00

		2001				2.90				3.03				3.09

		2002				2.79				3.06				3.19

		2003				2.70				3.09				3.29

		2004				2.60				3.12				3.39

		2005				2.51		-3.50%		3.15		1.00%		3.49		3.10%

		2006				2.42				3.21				3.60

		2007				2.34				3.26				3.71

		2008				2.26				3.32				3.83

		2009				2.18				3.37				3.95

		2010				2.10		-3.50%		3.43		1.70%		4.07		3.10%																				-0.0220672315		-0.0141308314		RATE OF TRANSMISSION PRICE inCREASE 2000--2010

		2011				2.15				3.51				4.18

		2012				2.19				3.60				4.29

		2013				2.24				3.68				4.41

		2014				2.29				3.77				4.53

		2015				2.34		2.20%		3.86		2.40%		4.65		2.70%

		2016				2.39				3.95				4.78

		2017				2.45				4.05				4.91

		2018				2.50				4.15				5.04

		2019				2.56				4.25				5.17

		2020				2.61		2.20%		4.35		2.40%		5.31		2.70%																				-0.015		-0.01		Rate of Transmission price increase 2010-2020





del price

		

						DELIVERED PRICES FOR GAS FOR COGENERATION

						LOW, BASE AND HIGH CASES

						(All prices in $2000/Mcf)

																						<500 kW

						>50 MW								10 MW										Sudbury						Toronto

		YEAR				Low		Base		High				Low		Base		High				Low		Base		High		Low		Base		High

		2000				4.38		4.38		4.38				4.78		4.78		4.78				6.48		6.48		6.48		6.73		6.73		6.73

		2001				4.26		4.40		4.46				4.66		4.80		4.86				6.31		6.44		6.50		6.55		6.69		6.75

		2002				4.15		4.41		4.54				4.55		4.81		4.94				6.14		6.40		6.53		6.38		6.64		6.77

		2003				4.03		4.43		4.63				4.43		4.83		5.03				5.97		6.37		6.56		6.21		6.60		6.80

		2004				3.93		4.45		4.72				4.33		4.85		5.12				5.81		6.33		6.60		6.04		6.56		6.83

		2005				3.82		4.47		4.81				4.22		4.87		5.21				5.66		6.30		6.64		5.88		6.53		6.87

		2006				3.72		4.51		4.90				4.12		4.91		5.30				5.51		6.29		6.69		5.73		6.51		6.91

		2007				3.62		4.55		5.00				4.02		4.95		5.40				5.36		6.29		6.74		5.58		6.50		6.95

		2008				3.53		4.59		5.10				3.93		4.99		5.50				5.22		6.28		6.80		5.43		6.49		7.00

		2009				3.44		4.64		5.21				3.84		5.04		5.61				5.08		6.28		6.86		5.29		6.48		7.06

		2010				3.35		4.68		5.32				3.75		5.08		5.72				4.95		6.28		6.92		5.15		6.48		7.12

		2011				3.39		4.75		5.42				3.79		5.15		5.82				4.96		6.32		6.99		5.16		6.52		7.19

		2012				3.43		4.83		5.53				3.83		5.23		5.93				4.97		6.37		7.07		5.16		6.56		7.26

		2013				3.47		4.91		5.63				3.87		5.31		6.03				4.98		6.42		7.15		5.17		6.61		7.34

		2014				3.51		4.99		5.75				3.91		5.39		6.15				4.99		6.47		7.23		5.18		6.66		7.42

		2015				3.55		5.07		5.86				3.95		5.47		6.26				5.01		6.52		7.31		5.19		6.71		7.50

		2016				3.59		5.16		5.98				3.99		5.56		6.38				5.02		6.58		7.40		5.20		6.76		7.59

		2017				3.64		5.24		6.10				4.04		5.64		6.50				5.04		6.64		7.50		5.22		6.82		7.68

		2018				3.68		5.33		6.22				4.08		5.73		6.62				5.06		6.70		7.59		5.23		6.88		7.77

		2019				3.73		5.42		6.35				4.13		5.82		6.75				5.08		6.77		7.70		5.25		6.94		7.87

		2020				3.78		5.52		6.48				4.18		5.92		6.88				5.10		6.84		7.80		5.27		7.01		7.97





Sheet3

		

								1995		1996		1997		1998		1999

		Average Empress (US$)						0.88		1.1		1.43		1.51		1.94				0.76								2.42

		C$/US$						0.7286		0.7334		0.7222		0.6741		0.6711				0.7286		0.7334		0.7222		0.6741		0.6711

		Average Empress (C$)						1.2077957727		1.4998636488		1.980060925		2.2400237354		2.8907763374				1.0430963492		0		0		0		3.6060199672

		% change								24.2%		32.0%		13.1%		29.1%

		NEB Price Analysis						2000		2005		2010		2015		2020		2025

		Case 1

		Alberta Border, $/GJ						1.91				1.99						2.75

		Alberta Border, $/Mcf						2.01505				2.09945						2.90125

		% growth										0.41%						2.18%

		Case 2

		Alberta Border, $/GJ						1.91				2.6						3.86

		Alberta Border, $/Mcf						2.01505				2.743						4.0723

		% growth										3.13%						2.67%

																		2.42%

								Note: NEB document says average price growth in Case 1 is 1.5%; in Case 2, 2.8%.  Assuming those rates from 2000 to 2025

								and using final values to infer backwards, Case 1 has 2000 price of about $1.89; Case 2 has a price of $1.93 ($/GJ).  The price is taken in

								the middle, under the assumption that there were rounding errors in both growth rates quoted.

		NEB Ontario price analysis

		Case 1 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		23.78		22.62		22.62		23.06		23.52

		% growth						-1.61%		-2.00%		-1.00%		0.00%		0.39%		0.40%

		gas				9.48		10.49		10.25		10.39		10.78		11.25		11.65

		% growth						2.05%		-0.46%		0.27%		0.74%		0.86%		0.70%

		commercial

		Elec				23.56		21.73		19.64		18.68		18.68		19.05		19.42

		% growth						-1.60%		-2.00%		-1.00%		0.00%		0.39%		0.39%

		gas				7.1		8.21		8.01		8.13		8.51		9.05		9.52

		% growth						2.95%		-0.49%		0.30%		0.92%		1.24%		1.02%

		industrial

		Elec				21.27		19.62		17.73		16.86		16.86		17.19		17.53

		% growth						-1.60%		-2.01%		-1.00%		0.00%		0.39%		0.39%

		gas				4.19		5.18		5.1		5.27		5.65		6.18		6.64

		% growth						4.33%		-0.31%		0.66%		1.40%		1.81%		1.45%

		Case 2 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		25.27		25.27		25.9		26.54		27.19

		% growth						-1.61%		-0.80%		0.00%		0.49%		0.49%		0.49%

		gas				9.48		10.79		10.87		11.19		11.9		12.72		13.05

		% growth						2.62%		0.15%		0.58%		1.24%		1.34%		0.51%

		commercial

		Elec				23.56		21.73		20.87		20.87		21.39		21.91		22.46

		% growth						-1.60%		-0.80%		0.00%		0.49%		0.48%		0.50%

		gas				7.1		8.58		8.75		9.03		9.71		10.49		10.77

		% growth						3.86%		0.39%		0.63%		1.46%		1.56%		0.53%

		industrial

		Elec				21.27		19.62		18.84		18.84		19.31		19.78		20.27

		% growth						-1.60%		-0.81%		0.00%		0.49%		0.48%		0.49%

		gas				4.19		5.54		5.84		6.24		6.98		7.84		8.27

		% growth						5.74%		1.06%		1.33%		2.27%		2.35%		1.07%

		EIA Price Analysis						2000		2005		2010		2015		2020		2025

		Economic Growth Case

		Well price, lower 48, $/Mcf						2.11		2.52		2.71		2.91		3.09

		Import price						2.2		2.45		2.6		2.72		2.88

		% growth (import)								2.18%		1.20%		0.91%		1.15%

		Reference Case

		Well price, lower 48, $/Mcf						2.1		2.35		2.52		2.62		2.68

		Import price						2.19		2.36		2.48		2.55		2.68

		% growth (import)								1.51%		1.00%		0.56%		1.00%

		Oil Price Case

		Well price, lower 48, $/Mcf						2.12		2.41		2.52		2.64		2.7

		Import price						2.2		2.42		2.54		2.61		2.73

		% growth (import)								1.92%		0.97%		0.55%		0.90%

								0.12178		$/M3

								28		MCF/M3

								3.40984






_1011610459.xls
Base

		

		Table 2.1

		Large and Medium Cogeneration Technologies

		Estimated Generating Costs

		Base Case Gas Prices

		Type of Unit				Rated				Fuel		Capital		Levelized		Levelized		Total		Steam Credit		Availability		Levelized		LUEC without		Levelized		LUEC with

						Output								O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)						(C$/kW)		(C$/kW)		(C$/kW)		(Btu/kWh)		(Btu/kWh)				(C$/kW)		(C$/kW)		(C$/kW)		(C$/kW)

				Gas Turbine		CCC		250		Gas		774		4.96		34.73		6,705		< 6,000		93.0%		1.27		50.82		4.21		46.72

						SCC		250		Gas		814		4.97		54.41		10,506		4,330		93.0%		1.52		70.62		32.69		38.80

						CCC		150		Gas		813		6.25		39.95		7,715		< 6,000		93.0%		1.36		57.80		9.33		48.71

						CCC		100		Gas		1,131		9.36		38.94		7,519		< 6,000		93.0%		2.10		64.88		8.65		56.46

						CCC		50		Gas		1,626		18.61		37.61		7,262		< 6,000		93.0%		3.25		80.55		6.98		73.76

						SCC		40		Gas		1,290		17.29		44.81		8,652		4,350		93.0%		2.65		81.00		24.78		56.88

						SCC		26		Gas		1,563		20.37		56.01		10,815		4,840		93.0%		3.29		99.23		36.40		63.80

						SCC		10		Gas		1,600		20.68		62.50		11,124		4,780		93.0%		3.35		106.58		39.35		68.19

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*										SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*										SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*										SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*										SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible

																																								LUEC without		LUEC with

																																								Steam Credit		Steam Credit

																																						Unit Type		(Cdn$/MWh)		(Cdn$/MWh)

																																						CCC250		50.82		46.72

																																						SCC250		70.62		38.80

																																						CCC150		57.80		48.71

																																						CCC100		64.88		56.46

																																						CCC50		80.55		73.76

																																						SCC40		81.00		56.88

																																						SCC26		99.23		63.80

																																						SCC10		106.58		68.19





Base

		CCC250		CCC250

		SCC250		SCC250

		CCC150		CCC150

		CCC100		CCC100

		CCC50		CCC50

		SCC40		SCC40

		SCC26		SCC26

		SCC10		SCC10



LUEC without Steam Credit

LUEC with Steam Credit

Unit Type

(Cdn$/Mwh)

LUEC of different generation options

50.82

46.72

70.62

38.8

57.8

48.71

64.88

56.46

80.55

73.76

81

56.88

99.23

63.8

106.58

68.19



Low

		

		Cogeneration Potential in Ontario

		Estimated Generating Costs

		Type of Unit				Rated Output				Fuel				Levelized		Levelized		Plant		Class 43		Availability		Levelized		LUEC without		Levelized		LUEC with

														O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)						(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

				Gas Turbine		CCC		250		Gas		774		4.96		27.29		6,705		< 6,000		93.0%		2.17		44.95		3.30		41.57

						SCC		250		Gas		814		4.97		42.76		10,506		4,330		93.0%		2.15		61.44		25.69		35.14

						CCC		150		Gas		813		6.25		44.29		7,715		< 6,000		93.0%		0.89		61.20		10.34		51.31

						CCC		100		Gas		1,131		9.36		30.60		7,519		< 6,000		93.0%		2.99		58.30		6.79		51.35

						CCC		50		Gas		1,626		18.61		29.55		7,262		< 6,000		93.0%		4.15		74.20		5.48		68.59

						SCC		40		Gas		1,290		17.29		35.21		8,652		4,350		93.0%		3.24		73.44		19.47		53.50

						SCC		26		Gas		1,563		20.37		44.01		10,815		4,840		93.0%		3.87		103.98		28.60		60.49

						SCC		10		Gas		1,600		20.68		50.16		11,124		4,780		93.0%		3.97		96.85		31.59		64.59

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*										SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*										SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*										SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*										SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible																												Hagler Bailly Low Gas Price Forecast

																																								LUEC without		LUEC with

																																								Steam Credit		Steam Credit

																																						Unit Type		(Cdn$/MWh)		(Cdn$/MWh)

																																						CCC250		44.95		41.57

																																						SCC250		61.44		35.14

																																						CCC150		61.20		51.31

																																						CCC100		58.30		51.35

																																						CCC50		74.20		68.59

																																						SCC40		73.44		53.50

																																						SCC26		103.98		60.49

																																						SCC10		96.85		64.59



Mitchell P. Rothman:



Low

		CCC250		CCC250

		SCC250		SCC250

		CCC150		CCC150

		CCC100		CCC100

		CCC50		CCC50

		SCC40		SCC40

		SCC26		SCC26

		SCC10		SCC10



LUEC without Steam Credit

LUEC with Steam Credit

Unit Type

(Cdn$/Mwh)

LUEC of different generation options (Low Gas Price)

50.82

46.72

70.62

38.8

57.8

48.71

64.88

56.46

80.55

73.76

81

56.88

99.23

63.8

106.58

68.19



High

		

		Cogeneration Potential in Ontario

		Estimated Generating Costs

		Type of Unit				Rated Output				Fuel				Levelized		Levelized		Plant		Class 43		Availability		Levelized		LUEC without		Levelized		LUEC with

														O&M Cost		Fuel Cost				Heat Rate								Thermal Credit

						(MW)						(Cdn$/kW)		(Cdn$/MWh)		(Cdn$/MWh)		(Btu/kWh)		(Btu/kWh)				(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)		(Cdn$/MWh)

				Gas Turbine		CCC		250		Gas		774		4.96		38.49		6,705		< 6,000		93.0%		0.80		53.77		4.66		49.31

						SCC		250		Gas		814		4.97		60.31		10,506		4,330		93.0%		1.18		75.40		36.24		40.64

						CCC		150		Gas		813		6.25		31.40		7,715		< 6,000		93.0%		2.26		51.05		7.33		43.54

						CCC		100		Gas		1,131		9.36		43.17		7,519		< 6,000		93.0%		1.64		68.18		9.58		59.03

						CCC		50		Gas		1,626		18.61		41.69		7,262		< 6,000		93.0%		2.78		83.74		7.73		76.35

						SCC		40		Gas		1,290		17.29		49.67		8,652		4,350		93.0%		2.34		84.80		27.47		58.58

						SCC		26		Gas		1,563		20.37		62.09		10,815		4,840		93.0%		2.99		89.77		40.35		65.47

						SCC		10		Gas		1,600		20.68		68.76		11,124		4,780		93.0%		3.02		111.47		43.29		70.00

		Note:

		Legend:

		CCC250 - 250MW Combined Cycle Cogeneration*										SCC250 - 250MW Simple Cycle Cogeneration*

		CCC150 - 150MW Combined Cycle Cogeneration*										SCC40   - 40MW Simple Cycle Cogeneration*

		CCC100 - 100MW Combined Cycle Cogeneration*										SCC26   - 26MW Simple Cycle Cogeneration*

		CCC50   - 50 MW Combined Cycle Cogeneration*										SCC10   - 10MW Simple Cycle Cogeneration*

		* Class 43.1 eligible																												Hagler Bailly High Gas Price Forecast

																																								LUEC without		LUEC with

																																								Steam Credit		Steam Credit

																																						Unit Type		(Cdn$/MWh)		(Cdn$/MWh)

																																						CCC250		53.77		49.31

																																						SCC250		75.40		40.64

																																						CCC150		51.05		43.54

																																						CCC100		68.18		59.03

																																						CCC50		83.74		76.35

																																						SCC40		84.80		58.58

																																						SCC26		89.77		65.47

																																						SCC10		111.47		70.00





High

		CCC250		CCC250

		SCC250		SCC250

		CCC150		CCC150

		CCC100		CCC100

		CCC50		CCC50

		SCC40		SCC40

		SCC26		SCC26

		SCC10		SCC10



LUEC without Steam Credit

LUEC with Steam Credit

Unit Type

(Cdn$/Mwh)

LUEC of different generation options (High Gas Price)

50.82

46.72

70.62

38.8

57.8

48.71

64.88

56.46

80.55

73.76

81

56.88

99.23

63.8

106.58

68.19



Escalation

		Delivered prices for Gas for Cogeneration

		Low, Base and High Cases

		(All prices in Year 2000)

				>50MW												10MW

				Low				Base				High				Low				Base				High

		Year		($/Mcf)				($/Mcf)				($/Mcf)				($/Mcf)				($/Mcf)				($/Mcf)

		2000		4.38				4.38				4.38				4.78				4.78				4.78

		2001		4.26		-2.74%		4.40		0.46%		4.46		1.83%		4.66		-2.51%		4.8		0.42%		4.86		1.67%

		2002		4.15		-2.58%		4.41		0.23%		4.54		1.79%		4.55		-2.36%		4.81		0.21%		4.94		1.65%

		2003		4.03		-2.89%		4.43		0.45%		4.63		1.98%		4.43		-2.64%		4.83		0.42%		5.03		1.82%

		2004		3.93		-2.48%		4.45		0.45%		4.72		1.94%		4.33		-2.26%		4.85		0.41%		5.12		1.79%

		2005		3.82		-2.80%		4.47		0.45%		4.81		1.91%		4.22		-2.54%		4.87		0.41%		5.21		1.76%

		2006		3.72		-2.62%		4.51		0.89%		4.90		1.87%		4.12		-2.37%		4.91		0.82%		5.3		1.73%

		2007		3.62		-2.69%		4.55		0.89%		5.00		2.04%		4.02		-2.43%		4.95		0.81%		5.4		1.89%

		2008		3.53		-2.49%		4.59		0.88%		5.10		2.00%		3.93		-2.24%		4.99		0.81%		5.5		1.85%

		2009		3.44		-2.55%		4.64		1.09%		5.21		2.16%		3.84		-2.29%		5.04		1.00%		5.61		2.00%

		2010		3.35		-2.62%		4.68		0.86%		5.32		2.11%		3.75		-2.34%		5.08		0.79%		5.72		1.96%

		2011		3.39		1.19%		4.75		1.50%		5.42		1.88%		3.79		1.07%		5.15		1.38%		5.82		1.75%

		2012		3.43		1.18%		4.83		1.68%		5.53		2.03%		3.83		1.06%		5.23		1.55%		5.93		1.89%

		2013		3.47		1.17%		4.91		1.66%		5.63		1.81%		3.87		1.04%		5.31		1.53%		6.03		1.69%

		2014		3.51		1.15%		4.99		1.63%		5.75		2.13%		3.91		1.03%		5.39		1.51%		6.15		1.99%

		2015		3.55		1.14%		5.07		1.60%		5.86		1.91%		3.95		1.02%		5.47		1.48%		6.26		1.79%

		2016		3.59		1.13%		5.16		1.78%		5.98		2.05%		3.99		1.01%		5.56		1.65%		6.38		1.92%

		2017		3.64		1.39%		5.24		1.55%		6.10		2.01%		4.04		1.25%		5.64		1.44%		6.5		1.88%

		2018		3.68		1.10%		5.33		1.72%		6.22		1.97%		4.08		0.99%		5.73		1.60%		6.62		1.85%

		2019		3.73		1.36%		5.42		1.69%		6.35		2.09%		4.13		1.23%		5.82		1.57%		6.75		1.96%

		2020		3.78		1.34%		5.52		1.85%		6.48		2.05%		4.18		1.21%		5.92		1.72%		6.88		1.93%

		Average				-0.72%				1.16%				1.98%				-0.65%				1.08%				1.84%

		Minimum				-2.89%				0.23%				1.79%				-2.64%				0.21%				1.65%

		Maximum				1.39%				1.85%				2.16%				1.25%				1.72%				2.00%





InputData

				Capacity						Cogen Steam Flow								Heat Rate (LHV)								Capital

				Summer		Winter		Average		Summer		Winter		Average								Include Degradation 3%

				MW		MW		MW		kpph		kpph		kpph		MJ/sec		Btu/kWh		kJ/kWh		Btu/kWh		kJ/kWh		Cdn$		Cdn$/kW

		CC500		495.00		535.00		515.00										6300		6,647		6,489		6,847		326,631,000		634

		CC250		250.00		270.00		260.00										6250		6,594		6,438		6,792		190,617,000		733

		CCC250		242.00		257.00		249.50		120		140		130.00		45.72		6510		6,869		6,705		7,075		193,100,000		774

		SCC250		223.00		246.00		234.50		939.7		960		949.85		334.06		10200		10,762		10,506		11,085		191,000,000		814

		CCC150		154.00		166.00		160.00		175		195		185.00		65.06		7490		7,903		7,715		8,140		130,008,000		813

		CCC100		92.60		99.70		96.15		100		106		103.00		36.23		7300		7,702		7,519		7,933		108,748,000		1,131

		CCC50		43.20		50.50		46.85		40		41		40.50		14.24		7050		7,438		7,262		7,662		76,180,000		1,626

		CCC40		38.50		46.50		42.50		126		135		130.50		45.90		8400		8,863		8,652		9,129		54,831,000		1,290

		CCC26		24.00		27.00		25.50		114		116		115.00		40.45		10500		11,079		10,815		11,411		39,852,000		1,563

		CCC10		10.00		11.00		10.50		51		52		51.50		18.11		10800		11,395		11,124		11,737		21,405,000		2,039





Sensitivity

		

		Table 4.1

		Cogeneration Potential in Ontario

		Sensitivity Analysis based on 250MW Combined Cycle Cogeneration Case (CCC250 )

		Parameter Changed		Changed		LUEC without		LUEC with		IRR

						(Cdn$/MWh)		(Cdn$/MWh)		(%)

		Base Case		46.72 Cdn$/MWh		50.82		46.72		13.00

		Electricity Rate		38.00 Cdn$/MWh		-		-

				45.00 Cdn$/MWh		-		-		0.74

				50.00 Cdn$/MWh		-		-		25.47

		Heat Rate		-5%		49.13		45.03		13.00

				-10%		47.44		43.34		13.00

		Capital Cost		-5%		50.21		46.12		13.00

				-10%		49.61		45.52		13.00

		Note:





5cents

		

		Cogeneration Potential in Ontario

		Results of IRR with electricity rate at 50.00 Cdn$/MWh

		Type of Unit				Rated Output				IRR

						(MW)				(%)

		Cogeneration

				Gas Turbine		CCC		250		25.47

						SCC		250		43.57

						CCC		150		18.62

						CCC		100		N/A

						CCC		50		N/A

						SCC		40		N/A

						SCC		26		N/A

						SCC		10		N/A






_1003823285.xls
tolls

		

						DISTRIBUTION AND TRANSMISSION CHARGES

						(All prices in $2000/Mcf)

										Distribution Tariffs for Cogeneration

						Transmission				>50 MW				10 MW				<500 kW

		YEAR				Tolls				Sudbury		Toronto		Sudbury		Toronto		Sudbury		Toronto

		2000				0.98				0.40		0.40		0.80		0.80		2.50		2.75

		2001				0.97				0.40		0.40		0.80		0.80		2.44		2.69

		2002				0.95				0.40		0.40		0.80		0.80		2.39		2.63

		2003				0.94				0.40		0.40		0.80		0.80		2.34		2.57

		2004				0.93				0.40		0.40		0.80		0.80		2.29		2.52

		2005				0.91				0.40		0.40		0.80		0.80		2.24		2.46

		2006				0.90				0.40		0.40		0.80		0.80		2.19		2.41

		2007				0.89				0.40		0.40		0.80		0.80		2.14		2.35

		2008				0.87				0.40		0.40		0.80		0.80		2.09		2.30

		2009				0.86				0.40		0.40		0.80		0.80		2.05		2.25

		2010				0.85				0.40		0.40		0.80		0.80		2.00		2.20

		2011				0.84				0.40		0.40		0.80		0.80		1.97		2.17

		2012				0.83				0.40		0.40		0.80		0.80		1.94		2.13

		2013				0.82				0.40		0.40		0.80		0.80		1.91		2.10

		2014				0.82				0.40		0.40		0.80		0.80		1.88		2.07

		2015				0.81				0.40		0.40		0.80		0.80		1.85		2.04

		2016				0.80				0.40		0.40		0.80		0.80		1.83		2.01

		2017				0.79				0.40		0.40		0.80		0.80		1.80		1.98

		2018				0.78				0.40		0.40		0.80		0.80		1.77		1.95

		2019				0.78				0.40		0.40		0.80		0.80		1.75		1.92

		2020				0.77				0.40		0.40		0.80		0.80		1.72		1.89





gas prices

		

						FORECAST GAS PRICES

										Alberta Border

						(All prices in $2000/Mcf)

						LOW CASE				BASE CASE				HIGH CASE

								5 yr				5 yr				5 yr

		YEAR				$		AAGR		$		AAGR		$		AAGR

		2000				3.00				3.00				3.00

		2001				2.90				3.03				3.09

		2002				2.79				3.06				3.19

		2003				2.70				3.09				3.29

		2004				2.60				3.12				3.39

		2005				2.51		-3.50%		3.15		1.00%		3.49		3.10%

		2006				2.42				3.21				3.60

		2007				2.34				3.26				3.71

		2008				2.26				3.32				3.83

		2009				2.18				3.37				3.95

		2010				2.10		-3.50%		3.43		1.70%		4.07		3.10%																				-0.0220672315		-0.0141308314		RATE OF TRANSMISSION PRICE inCREASE 2000--2010

		2011				2.15				3.51				4.18

		2012				2.19				3.60				4.29

		2013				2.24				3.68				4.41

		2014				2.29				3.77				4.53

		2015				2.34		2.20%		3.86		2.40%		4.65		2.70%

		2016				2.39				3.95				4.78

		2017				2.45				4.05				4.91

		2018				2.50				4.15				5.04

		2019				2.56				4.25				5.17

		2020				2.61		2.20%		4.35		2.40%		5.31		2.70%																				-0.015		-0.01		Rate of Transmission price increase 2010-2020





del price

		

						DELIVERED PRICES FOR GAS FOR COGENERATION

						LOW, BASE AND HIGH CASES

						(All prices in $2000/Mcf)

																						<500 kW

						>50 MW								10 MW										Sudbury						Toronto

		YEAR				Low		Base		High				Low		Base		High				Low		Base		High		Low		Base		High

		2000				4.38		4.38		4.38				4.78		4.78		4.78				6.48		6.48		6.48		6.73		6.73		6.73

		2001				4.26		4.40		4.46				4.66		4.80		4.86				6.31		6.44		6.50		6.55		6.69		6.75

		2002				4.15		4.41		4.54				4.55		4.81		4.94				6.14		6.40		6.53		6.38		6.64		6.77

		2003				4.03		4.43		4.63				4.43		4.83		5.03				5.97		6.37		6.56		6.21		6.60		6.80

		2004				3.93		4.45		4.72				4.33		4.85		5.12				5.81		6.33		6.60		6.04		6.56		6.83

		2005				3.82		4.47		4.81				4.22		4.87		5.21				5.66		6.30		6.64		5.88		6.53		6.87

		2006				3.72		4.51		4.90				4.12		4.91		5.30				5.51		6.29		6.69		5.73		6.51		6.91

		2007				3.62		4.55		5.00				4.02		4.95		5.40				5.36		6.29		6.74		5.58		6.50		6.95

		2008				3.53		4.59		5.10				3.93		4.99		5.50				5.22		6.28		6.80		5.43		6.49		7.00

		2009				3.44		4.64		5.21				3.84		5.04		5.61				5.08		6.28		6.86		5.29		6.48		7.06

		2010				3.35		4.68		5.32				3.75		5.08		5.72				4.95		6.28		6.92		5.15		6.48		7.12

		2011				3.39		4.75		5.42				3.79		5.15		5.82				4.96		6.32		6.99		5.16		6.52		7.19

		2012				3.43		4.83		5.53				3.83		5.23		5.93				4.97		6.37		7.07		5.16		6.56		7.26

		2013				3.47		4.91		5.63				3.87		5.31		6.03				4.98		6.42		7.15		5.17		6.61		7.34

		2014				3.51		4.99		5.75				3.91		5.39		6.15				4.99		6.47		7.23		5.18		6.66		7.42

		2015				3.55		5.07		5.86				3.95		5.47		6.26				5.01		6.52		7.31		5.19		6.71		7.50

		2016				3.59		5.16		5.98				3.99		5.56		6.38				5.02		6.58		7.40		5.20		6.76		7.59

		2017				3.64		5.24		6.10				4.04		5.64		6.50				5.04		6.64		7.50		5.22		6.82		7.68

		2018				3.68		5.33		6.22				4.08		5.73		6.62				5.06		6.70		7.59		5.23		6.88		7.77

		2019				3.73		5.42		6.35				4.13		5.82		6.75				5.08		6.77		7.70		5.25		6.94		7.87

		2020				3.78		5.52		6.48				4.18		5.92		6.88				5.10		6.84		7.80		5.27		7.01		7.97





Sheet3

		

								1995		1996		1997		1998		1999

		Average Empress (US$)						0.88		1.1		1.43		1.51		1.94				0.76								2.42

		C$/US$						0.7286		0.7334		0.7222		0.6741		0.6711				0.7286		0.7334		0.7222		0.6741		0.6711

		Average Empress (C$)						1.2077957727		1.4998636488		1.980060925		2.2400237354		2.8907763374				1.0430963492		0		0		0		3.6060199672

		% change								24.2%		32.0%		13.1%		29.1%

		NEB Price Analysis						2000		2005		2010		2015		2020		2025

		Case 1

		Alberta Border, $/GJ						1.91				1.99						2.75

		Alberta Border, $/Mcf						2.01505				2.09945						2.90125

		% growth										0.41%						2.18%

		Case 2

		Alberta Border, $/GJ						1.91				2.6						3.86

		Alberta Border, $/Mcf						2.01505				2.743						4.0723

		% growth										3.13%						2.67%

																		2.42%

								Note: NEB document says average price growth in Case 1 is 1.5%; in Case 2, 2.8%.  Assuming those rates from 2000 to 2025

								and using final values to infer backwards, Case 1 has 2000 price of about $1.89; Case 2 has a price of $1.93 ($/GJ).  The price is taken in

								the middle, under the assumption that there were rounding errors in both growth rates quoted.

		NEB Ontario price analysis

		Case 1 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		23.78		22.62		22.62		23.06		23.52

		% growth						-1.61%		-2.00%		-1.00%		0.00%		0.39%		0.40%

		gas				9.48		10.49		10.25		10.39		10.78		11.25		11.65

		% growth						2.05%		-0.46%		0.27%		0.74%		0.86%		0.70%

		commercial

		Elec				23.56		21.73		19.64		18.68		18.68		19.05		19.42

		% growth						-1.60%		-2.00%		-1.00%		0.00%		0.39%		0.39%

		gas				7.1		8.21		8.01		8.13		8.51		9.05		9.52

		% growth						2.95%		-0.49%		0.30%		0.92%		1.24%		1.02%

		industrial

		Elec				21.27		19.62		17.73		16.86		16.86		17.19		17.53

		% growth						-1.60%		-2.01%		-1.00%		0.00%		0.39%		0.39%

		gas				4.19		5.18		5.1		5.27		5.65		6.18		6.64

		% growth						4.33%		-0.31%		0.66%		1.40%		1.81%		1.45%

		Case 2 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		25.27		25.27		25.9		26.54		27.19

		% growth						-1.61%		-0.80%		0.00%		0.49%		0.49%		0.49%

		gas				9.48		10.79		10.87		11.19		11.9		12.72		13.05

		% growth						2.62%		0.15%		0.58%		1.24%		1.34%		0.51%

		commercial

		Elec				23.56		21.73		20.87		20.87		21.39		21.91		22.46

		% growth						-1.60%		-0.80%		0.00%		0.49%		0.48%		0.50%

		gas				7.1		8.58		8.75		9.03		9.71		10.49		10.77

		% growth						3.86%		0.39%		0.63%		1.46%		1.56%		0.53%

		industrial

		Elec				21.27		19.62		18.84		18.84		19.31		19.78		20.27

		% growth						-1.60%		-0.81%		0.00%		0.49%		0.48%		0.49%

		gas				4.19		5.54		5.84		6.24		6.98		7.84		8.27

		% growth						5.74%		1.06%		1.33%		2.27%		2.35%		1.07%

		EIA Price Analysis						2000		2005		2010		2015		2020		2025

		Economic Growth Case

		Well price, lower 48, $/Mcf						2.11		2.52		2.71		2.91		3.09

		Import price						2.2		2.45		2.6		2.72		2.88

		% growth (import)								2.18%		1.20%		0.91%		1.15%

		Reference Case

		Well price, lower 48, $/Mcf						2.1		2.35		2.52		2.62		2.68

		Import price						2.19		2.36		2.48		2.55		2.68

		% growth (import)								1.51%		1.00%		0.56%		1.00%

		Oil Price Case

		Well price, lower 48, $/Mcf						2.12		2.41		2.52		2.64		2.7

		Import price						2.2		2.42		2.54		2.61		2.73

		% growth (import)								1.92%		0.97%		0.55%		0.90%

								0.12178		$/M3

								28		MCF/M3

								3.40984






_1003820220.xls
tolls

		

						DISTRIBUTION AND TRANSMISSION CHARGES

						(All prices in $2000/Mcf)

										Distribution Tariffs for Cogeneration

						Transmission				>50 MW				10 MW				<500 kW

		YEAR				Tolls				Sudbury		Toronto		Sudbury		Toronto		Sudbury		Toronto

		2000				0.98				0.40		0.40		0.80		0.80		2.50		2.75

		2001				0.97				0.40		0.40		0.80		0.80		2.44		2.69

		2002				0.95				0.40		0.40		0.80		0.80		2.39		2.63

		2003				0.94				0.40		0.40		0.80		0.80		2.34		2.57

		2004				0.93				0.40		0.40		0.80		0.80		2.29		2.52

		2005				0.91				0.40		0.40		0.80		0.80		2.24		2.46

		2006				0.90				0.40		0.40		0.80		0.80		2.19		2.41

		2007				0.89				0.40		0.40		0.80		0.80		2.14		2.35

		2008				0.87				0.40		0.40		0.80		0.80		2.09		2.30

		2009				0.86				0.40		0.40		0.80		0.80		2.05		2.25

		2010				0.85				0.40		0.40		0.80		0.80		2.00		2.20

		2011				0.84				0.40		0.40		0.80		0.80		1.97		2.17

		2012				0.83				0.40		0.40		0.80		0.80		1.94		2.13

		2013				0.82				0.40		0.40		0.80		0.80		1.91		2.10

		2014				0.82				0.40		0.40		0.80		0.80		1.88		2.07

		2015				0.81				0.40		0.40		0.80		0.80		1.85		2.04

		2016				0.80				0.40		0.40		0.80		0.80		1.83		2.01

		2017				0.79				0.40		0.40		0.80		0.80		1.80		1.98

		2018				0.78				0.40		0.40		0.80		0.80		1.77		1.95

		2019				0.78				0.40		0.40		0.80		0.80		1.75		1.92

		2020				0.77				0.40		0.40		0.80		0.80		1.72		1.89





gas prices

		

						FORECAST GAS PRICES

										Alberta Border

						(All prices in $2000/Mcf)

						LOW CASE				BASE CASE				HIGH CASE

								5 yr				5 yr				5 yr

		YEAR				$		AAGR		$		AAGR		$		AAGR

		2000				3.00				3.00				3.00

		2001				2.90				3.03				3.09

		2002				2.79				3.06				3.19

		2003				2.70				3.09				3.29

		2004				2.60				3.12				3.39

		2005				2.51		-3.50%		3.15		1.00%		3.49		3.10%

		2006				2.42				3.21				3.60

		2007				2.34				3.26				3.71

		2008				2.26				3.32				3.83

		2009				2.18				3.37				3.95

		2010				2.10		-3.50%		3.43		1.70%		4.07		3.10%																				-0.0220672315		-0.0141308314		RATE OF TRANSMISSION PRICE inCREASE 2000--2010

		2011				2.15				3.51				4.18

		2012				2.19				3.60				4.29

		2013				2.24				3.68				4.41

		2014				2.29				3.77				4.53

		2015				2.34		2.20%		3.86		2.40%		4.65		2.70%

		2016				2.39				3.95				4.78

		2017				2.45				4.05				4.91

		2018				2.50				4.15				5.04

		2019				2.56				4.25				5.17

		2020				2.61		2.20%		4.35		2.40%		5.31		2.70%																				-0.015		-0.01		Rate of Transmission price increase 2010-2020





del price

		

						DELIVERED PRICES FOR GAS FOR COGENERATION

						LOW, BASE AND HIGH CASES

						(All prices in $2000/Mcf)

																						<500 kW

						>50 MW								10 MW										Sudbury						Toronto

		YEAR				Low		Base		High				Low		Base		High				Low		Base		High		Low		Base		High

		2000				4.38		4.38		4.38				4.78		4.78		4.78				6.48		6.48		6.48		6.73		6.73		6.73

		2001				4.26		4.40		4.46				4.66		4.80		4.86				6.31		6.44		6.50		6.55		6.69		6.75

		2002				4.15		4.41		4.54				4.55		4.81		4.94				6.14		6.40		6.53		6.38		6.64		6.77

		2003				4.03		4.43		4.63				4.43		4.83		5.03				5.97		6.37		6.56		6.21		6.60		6.80

		2004				3.93		4.45		4.72				4.33		4.85		5.12				5.81		6.33		6.60		6.04		6.56		6.83

		2005				3.82		4.47		4.81				4.22		4.87		5.21				5.66		6.30		6.64		5.88		6.53		6.87

		2006				3.72		4.51		4.90				4.12		4.91		5.30				5.51		6.29		6.69		5.73		6.51		6.91

		2007				3.62		4.55		5.00				4.02		4.95		5.40				5.36		6.29		6.74		5.58		6.50		6.95

		2008				3.53		4.59		5.10				3.93		4.99		5.50				5.22		6.28		6.80		5.43		6.49		7.00

		2009				3.44		4.64		5.21				3.84		5.04		5.61				5.08		6.28		6.86		5.29		6.48		7.06

		2010				3.35		4.68		5.32				3.75		5.08		5.72				4.95		6.28		6.92		5.15		6.48		7.12

		2011				3.39		4.75		5.42				3.79		5.15		5.82				4.96		6.32		6.99		5.16		6.52		7.19

		2012				3.43		4.83		5.53				3.83		5.23		5.93				4.97		6.37		7.07		5.16		6.56		7.26

		2013				3.47		4.91		5.63				3.87		5.31		6.03				4.98		6.42		7.15		5.17		6.61		7.34

		2014				3.51		4.99		5.75				3.91		5.39		6.15				4.99		6.47		7.23		5.18		6.66		7.42

		2015				3.55		5.07		5.86				3.95		5.47		6.26				5.01		6.52		7.31		5.19		6.71		7.50

		2016				3.59		5.16		5.98				3.99		5.56		6.38				5.02		6.58		7.40		5.20		6.76		7.59

		2017				3.64		5.24		6.10				4.04		5.64		6.50				5.04		6.64		7.50		5.22		6.82		7.68

		2018				3.68		5.33		6.22				4.08		5.73		6.62				5.06		6.70		7.59		5.23		6.88		7.77

		2019				3.73		5.42		6.35				4.13		5.82		6.75				5.08		6.77		7.70		5.25		6.94		7.87

		2020				3.78		5.52		6.48				4.18		5.92		6.88				5.10		6.84		7.80		5.27		7.01		7.97





Sheet3

		

								1995		1996		1997		1998		1999

		Average Empress (US$)						0.88		1.1		1.43		1.51		1.94				0.76								2.42

		C$/US$						0.7286		0.7334		0.7222		0.6741		0.6711				0.7286		0.7334		0.7222		0.6741		0.6711

		Average Empress (C$)						1.2077957727		1.4998636488		1.980060925		2.2400237354		2.8907763374				1.0430963492		0		0		0		3.6060199672

		% change								24.2%		32.0%		13.1%		29.1%

		NEB Price Analysis						2000		2005		2010		2015		2020		2025

		Case 1

		Alberta Border, $/GJ						1.91				1.99						2.75

		Alberta Border, $/Mcf						2.01505				2.09945						2.90125

		% growth										0.41%						2.18%

		Case 2

		Alberta Border, $/GJ						1.91				2.6						3.86

		Alberta Border, $/Mcf						2.01505				2.743						4.0723

		% growth										3.13%						2.67%

																		2.42%

								Note: NEB document says average price growth in Case 1 is 1.5%; in Case 2, 2.8%.  Assuming those rates from 2000 to 2025

								and using final values to infer backwards, Case 1 has 2000 price of about $1.89; Case 2 has a price of $1.93 ($/GJ).  The price is taken in

								the middle, under the assumption that there were rounding errors in both growth rates quoted.

		NEB Ontario price analysis

		Case 1 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		23.78		22.62		22.62		23.06		23.52

		% growth						-1.61%		-2.00%		-1.00%		0.00%		0.39%		0.40%

		gas				9.48		10.49		10.25		10.39		10.78		11.25		11.65

		% growth						2.05%		-0.46%		0.27%		0.74%		0.86%		0.70%

		commercial

		Elec				23.56		21.73		19.64		18.68		18.68		19.05		19.42

		% growth						-1.60%		-2.00%		-1.00%		0.00%		0.39%		0.39%

		gas				7.1		8.21		8.01		8.13		8.51		9.05		9.52

		% growth						2.95%		-0.49%		0.30%		0.92%		1.24%		1.02%

		industrial

		Elec				21.27		19.62		17.73		16.86		16.86		17.19		17.53

		% growth						-1.60%		-2.01%		-1.00%		0.00%		0.39%		0.39%

		gas				4.19		5.18		5.1		5.27		5.65		6.18		6.64

		% growth						4.33%		-0.31%		0.66%		1.40%		1.81%		1.45%

		Case 2 ($/GJ, adjusted for efficiency)				1995		2000		2005		2010		2015		2020		2025

		residential

		Elec				28.53		26.31		25.27		25.27		25.9		26.54		27.19

		% growth						-1.61%		-0.80%		0.00%		0.49%		0.49%		0.49%

		gas				9.48		10.79		10.87		11.19		11.9		12.72		13.05

		% growth						2.62%		0.15%		0.58%		1.24%		1.34%		0.51%

		commercial

		Elec				23.56		21.73		20.87		20.87		21.39		21.91		22.46

		% growth						-1.60%		-0.80%		0.00%		0.49%		0.48%		0.50%

		gas				7.1		8.58		8.75		9.03		9.71		10.49		10.77

		% growth						3.86%		0.39%		0.63%		1.46%		1.56%		0.53%

		industrial

		Elec				21.27		19.62		18.84		18.84		19.31		19.78		20.27

		% growth						-1.60%		-0.81%		0.00%		0.49%		0.48%		0.49%

		gas				4.19		5.54		5.84		6.24		6.98		7.84		8.27

		% growth						5.74%		1.06%		1.33%		2.27%		2.35%		1.07%

		EIA Price Analysis						2000		2005		2010		2015		2020		2025

		Economic Growth Case

		Well price, lower 48, $/Mcf						2.11		2.52		2.71		2.91		3.09

		Import price						2.2		2.45		2.6		2.72		2.88

		% growth (import)								2.18%		1.20%		0.91%		1.15%

		Reference Case

		Well price, lower 48, $/Mcf						2.1		2.35		2.52		2.62		2.68

		Import price						2.19		2.36		2.48		2.55		2.68

		% growth (import)								1.51%		1.00%		0.56%		1.00%

		Oil Price Case

		Well price, lower 48, $/Mcf						2.12		2.41		2.52		2.64		2.7

		Import price						2.2		2.42		2.54		2.61		2.73

		% growth (import)								1.92%		0.97%		0.55%		0.90%

								0.12178		$/M3

								28		MCF/M3

								3.40984






