Public Water Supply Section, Division of Environmental Health (PWS) prepared this factsheet to provide directions on documenting pressure-related problems.  These problems may include low pressure or repeated outages.

The rule promulgated under the state bond act [15A NCAC 1J and 1L .0701(2)(b)(v)] is quoted below.  The wording for the federally funded drinking water state revolving fund loan program (DWSRF) [15A NCAC 1N .0602(2)(e)] is identical.

Projects that address documented recurrent water outages or low pressure below the requirements of 15A NCAC 18C .0901.  Only problems that affect human consumption of drinking water shall be considered for award of points under this criteria (sic).

15A 18C NCAC .0901 reads as follows:

Water distribution mains shall be sized to provide a minimum pressure at all points within the distribution system of not less than 20 pounds per square inch (gauge) during periods of peak demand (fire flow), but in any case water mains shall not be less than two-inch standard nominal diameter. Fire hydrants shall not be installed on water mains of less than six inches diameter or on water mains or water systems not designed to carry fire protection flows. Systems not designed for fire flows shall have the capacity to maintain a pressure of at least 30 pounds per square inch (gauge) throughout the system during periods of peak flow.

In summary, these regulations require that a system maintain 20 pounds per square inch (psi) at all times (even when under fire flow), and 30 psi except when under fire flow.

### Measurement Method

To determine if these standards are met, applicants typically open one fire hydrant while reading the pressure on a nearby hydrant.  Alternatively, applicants may place a continuous pressure recorder on various fixtures (e.g., fire hydrants) to determine the pressures encountered during routine operation.

### Documentation

The report documenting the pressure problems must explain in detail how each low pressure reading was obtained.

Please include a map showing the sampling location of each low pressure reading (or outage), including the following:

- the existing line,

- the proposed line,

- where the pressure was measured (typically, the closed hydrant), and

- anything that was manipulated during the measurement (typically, the open hydrant).

Please include the field data sheets and a brief explanation of what was done to generate each low pressure reading.  Since local fire departments do this testing routinely, many have pre-formatted data sheets.

In summary, you must demonstrate that the problem exists, and document how you determined the problem exists.  You must submit all raw data.

Note that the application (in particular, the Preliminary Engineering Report – PER) must adequately demonstrate that the proposed project will solve the problem you document.

### Project Design

You must ensure that you have enough pressure readings or outages to justify the entire project.   That is, the readings should be well spread out throughout the project area.  There must be at least one reading on every distinct stretch of line.

If some physically separate line does not have low pressure or outages, but needs to be replaced to fix a problem elsewhere (i.e., is hydraulically linked to a low pressure zone), then explain this linkage.

The number of pressure readings should be proportionate to the length of line.  PWS requests at least one pressure reading for each mile of line.  More readings may be required in highly built up areas.

An example of the recommended presentation follows:

Measurements were made of the static pressure (no flow pressure) of hydrants in the Minor Street Area by connecting a calibrated pressure gauge to the hydrants.  Simulated fire-flow pressure (residual pressure) was made by opening a nearby hydrant three and one half (3 1/2) turns and reading the residual pressure.

Two of the hydrants failed to meet requirements to maintain residual pressure of 20 psi under simulated fire flow conditions.  The hydrant in front of 6527 Minor Street just met the requirement.  These results clearly justify upsizing the lines on Elm and Post streets to 6-inch.  Note that all hydrants are installed on 4-inch line in violation of 15A NCAC 18C .0901 (which requires 6-inch line).

There have been six line breaks on the 6500 block of Minor Street since January 1998 (dates are documented in the attached repair work orders).  We will replace the line on Minor Street to complete the loop with the 12-inch supply main on Main Street, and to prevent future outages.

Field data sheets are attached to the back of this report.

Table 1.  Pressure testing results - Mains Street Area

| Location of Low P reading | Location of Open hydrant | Static (no flow) Pressure [psi] | Fire Flow (Residual) Pressure [psi] | Comments |
| --- | --- | --- | --- | --- |
| 6527 Minor Street | Corner Minor & Elm | 60 | 20 | marginally meets requirements, but multiple outages |
| Corner Minor & Elm | 6527 Minor Street | 58 | 13 | fails to meet requirements |
| 1300 Post Street | 6527 Elm Street | 45 | 11 | fails to meet requirements |