Fox                                                      Smart A/C Controller                                                       Listing 2

LISTING 2

This program is for the PICAXE-08M processor it insures that the

'compressor is protected with a 5 or 3 minute delay

'compressor is controlled by pin 2 and LED by pin 1

'uses B0,B1,B2,W6

'Pin3 = Compressor signal.

'Pin4 = Time delay signal

'6/19/2008 tested

'===Directives===

#com1		;specify which com port

#picaxe 08M	; specify which PICAXE chip

'=== Main Program =============

'uses B0,B1,B2,W6

'Pin3 = Compressor signal

'Pin4 = Time delay signal

symbol Compressor = b0		'state of compressor

symbol ComOn = 1			'constant

symbol ComOff = 0			'constant

testing:	low 1			'blink compressor led for visual test

pause 250

high 1

pause 250

low 1 pause 250

high 1 pause 250

main:low 2					'compressor pin; Off on start up

low 1					'LED pin; Off on start up

Compressor = ComOff		'compressor state; Off on start up

pause 50

do

'Only turn off compressor and LED if compressor is on

if pin3 = 0 and Compressor = ComOn then

low 2

low 1

Compressor = ComOff

endif

'Only turn on compressor and LED if compressor is off

if pin3 = 1 and Compressor = ComOff then

gosub OnCompressor

endif

pause 50

loop

OnCompressor:

'delay either 3 or 5 minutes(default)

for w6 = 1 to 600

if pin4 = 1 then

pause 200

endif

pause 300

B2 = w6 % 2

if B2 = 1 then

high 1

endif

if B2 = 0 then

low 1

endif

if pin3 = 0 then

low 1

Compressor = ComOff

return

endif

next w6

'turn on compressor

high 2

'turn on LED

high 1

Compressor = ComOn

return

end